H71	LEAD SHEET COVERINGS/ FLASHINGS

To be read with Preliminaries/ General conditions.

TYPES OF LEADWORK

H71/420	COVER FLASHINGS AT ABUTMENTS GENERALLY, AROUND RAINWATER CHUTES, AT EAVES OF ROOF OVER SUB-STATION, & AT JUNCTION OF RENDER AND BRICKWORK AT EXISTING EXTERNAL WALLS

-	Lead:

-	Thickness: Code 4 .

-	Dimensions:

-	Lengths: Not more than 1500mm .

-	End to end joints: Laps of not less than 100 mm.

-	Cover: Overlap to upstand of not less than 75 mm.

- Fixing: Lead wedges into brickwork mortar joints and lead dlips to bottom edge at laps and at 300mm centres.

GENERAL REQUIREMENTS/ PREPARATORY WORK

H71/510	WORKMANSHIP GENERALLY

-	Standard: To BS 6915 and latest edition of ‘Rolled lead sheet. The complete manual’ published by the Lead Sheet Association.

-	Fabrication and fixing: To provide a secure, free draining and weathertight installation.

-	Operatives: Trained in the application of lead coverings/ flashings. Submit records of experience on request.

-	Measuring, marking, cutting and forming: Prior to assembly wherever possible.

-	Marking out: With pencil, chalk or crayon. Do not use scribers or other sharp instruments without approval.

-	Bossing and forming: Straight and regular bends, leaving sheets free from ripples, kinks, buckling and cracks.

-	Solder: Use only where specified.

-	Sharp metal edges: Fold under or remove as work proceeds.

-	Finished work:  Fully supported, adequately fixed to resist wind uplift but also able to accommodate thermal movement without distortion or stress.

-	Protection: Prevent staining, discolouration and damage by subsequent works.

H71/515	LEADWELDING

-	In situ leadwelding: Not permitted.

H71/520	LEAD SHEET

-	Production method:

-	Rolled, to BS EN 12588, or

-	Machine cast, Agrément certified and to code thicknesses with a tolerance (by weight) of ±5%, or

-	Sand cast, from lead free from bitumen, solder, other impurities, inclusions, laminations, cracks, air, pinholes and blowholes; to code thicknesses but with a tolerance (by weight) of ±10%.

-	Identification: Labelled to show thickness/ code, weight and type.

H71/610	SUITABILITY OF SUBSTRATES

-	Condition: Dry and free of dust, debris, grease and other deleterious matter.

H71/640	TIMBER FOR USE WITH LEADWORK

-	Quality: Planed, free from wane, pitch pockets, decay and insect attack (ambrosia beetle excepted).

-	Moisture content: Not more than 22% at time of covering. Give notice if greater than 16%.

-	Preservative treatment: Organic solvent as section Z12 and British Wood Preserving and Damp-proofing Association Manual - Commodity Specification C8.

H71/650	UNDERLAY

-	Handling: Prevent tears and punctures.

-	Laying: Butt or overlap jointed onto a dry substrate.

-	Fixing edges: With copper or stainless steel staples or clout nails.

-	Do not lay over roof edges but do turn up at abutments.

-	Wood core rolls: Fixed over underlay.

-	Protection: Keep dry and cover with lead at the earliest opportunity.

FIXING LEAD

H71/715	CLIPS

-	Material:

-	Lead clips: Cut from sheets of same thickness/ code as sheet being secured.

-	Dimensions:

-	Width: 50 mm where not continuous.

-	Length: To suit detail.

-	Fixing clips: Secure each to substrate with two fixings not more than 50 mm from edge of lead sheet.

-	Fixing lead sheet: Welt clips around edges and turn over 25 mm.

H71/770	WEDGE FIXING INTO JOINTS/ CHASES

-	Joint/ Chase: Rake out to a depth of not less than 25 mm.

-	Lead: Dress into joint/ chase.

-	Fixing: Lead wedges at not more than 450 mm centres, at every change of direction and with at least two for each piece of lead.

- Sealant: Silicone.

- Application: As section Z22.

770/A	LEAD COUNTER-FLASHINGS (CHASES UP TO 18 MM WITHOUT A DPC)

- Location:  Counter-flashings to abutment upstands

- Thickness: 1.75 mm (Code 4) rolled lead sheet.

- Lengths:  these should not exceed 1500 mm when one edge is wedged and pointed into a chase in masonry.  Where lead flashings are built into bitumen sheet roofing (sandwiched between layers) the maximum length should be reduced to 1000 mm.

- Installation: All lead counter-flashing sections to be lapped by 150 mm and base clipped and lead wedges provided at 300 mm centres.  Exposed lead should be treated with Patination oil on completion, as clause 970.   All lead work should be carried out by competent tradesmen in accordance with current British Codes of Practice and Lead Development Association recommendations.

- Chase preparation:  Cut a chase in the mortar bed course (normally 10 mm approx.) to a depth of 25 mm, providing sufficent space to insert both the lead flashing and the wedges.  All chases  should  be  brushed  clean  and sealed  using  Bauder sealant primer prior to  the application  of the Bauder Mastic Sealant.

- Sealant: Bauder Mastic Sealant, colour: Grey.

780	LEAD COUNTER-FLASHINGS (CHASES UP TO 18 MM WHERE A DPC IS PRESENT)

- Location:  Counter-flashings to abutment  upstands

- Thickness: 1.75 mm (Code 4) rolled lead sheet.

- Lengths:  these should not exceed 1500 mm when one edge is wedged and pointed into a chase in masonry.  Where lead flashings are built into bitumen sheet roofing (sandwiched between layers) the maximum length should be reduced to 1000 mm.

- Installation: All lead counter-flashing sections to be lapped by 150 mm and base clipped and lead wedges provided at 300 mm centres.   Exposed lead should be treated with Patination oil on completion, as clause 970.   All lead work should be carried out by competent tradesmen in accordance with current British Codes of Practice and Lead Development Association recommendations.

- Chase preparation: Cut a chase in the mortar bed course (normally 10 mm width approx.) to a depth of 25 mm.  In addition, cut a rebate in the top of the brick course under the joint to increase the overall chase width to not more than 18 mm and to a depth of 25 mm, so that there is sufficent space to insert both the lead flashing and the wedges, without damaging the DPC.  All chases  should  be  brushed  clean  and sealed  using  Bauder sealant primer prior to  the application  of the Bauder Mastic Sealant.

- Sealant: Bauder Mastic Sealant, colour: Grey.

JOINTING LEAD

810B	SITE FABRICATED LEAD CHUTE OUTLETS

- Material: Code 4 lead, fabricated and installed in accordance with the Lead Development Association recommendations.

- Exposed lead should be treated with Patination oil, as clause 970, in accordance with the Lead Development Association recommendations.

- Fit a proprietary wire basket or plastic leaf guard upon completion.

H71/880	WELTED JOINTS

-	Joint allowance: 50 mm overlap and 25 mm underlap.

-	Copper or stainless steel clips: Fix to substrate at not more than 450 mm centres.

-	Overlap: Welt around underlap and clips and lightly dress down.

970	PATINATION OIL

- Patination oil should be used on lead where run off of rain water drains on to other materials which could be stained by the patina salts, e.g. slate and tile roofs, brick, concrete and stone walling.