F10	BRICK/ BLOCK WALLING

To be read with Preliminaries/ General conditions.

To be read in conjunction with Structural Engineer’s specification F10.

TYPES OF WALLING

F10/110/A	GLAZED FACING BRICKWORK ALL ALONG BOUNDARY WALL AT REAR OF PAVEMENT (FOR PLAYCENTRE EXTENSION, BELOW RAILINGS, AND FOR SUB-STATION

-	Bricks: To BS 3921.

-	Manufacturer: JHF Brick (UK) Ltd, 215 x 65 x 102, colour refs to be agreed, in accordance with EN771-1 & DIN 105

Product reference: To Architect’s approval.  Note, 2 colours to be selected in equal proportions.

-	Specials: glazed end bricks, copings and end copings.

-	Mortar: As section Z21.

-	Standard: To BS 4721.

-	Mix: 1:1:6 cement:lime:sand.

-	Additional requirements: N/A.

-	Bond: Stretcher, throughout, including where solid 215mm thick walls.

-	Joints: To match existing building .

- Features: N/A.

F10/110/B	CLAY FACING BRICKWORK ELSEWHERE TO NEW EXTENSIONS

-	Bricks: To BS 3921.

-	Manufacturer: Contractor’s choice to match existing school buildings at ground floor level.

Product reference: To Architect’s approval.

-	Special shapes: N/A .

-	Mortar: As section Z21.

-	Standard: To BS 4721.

-	Mix: 1:1:6 cement:lime:sand.

-	Additional requirements: N/A.

-	Bond: Stretcher, including where solid 215mm thick walls.

-	Joints: To match existing building .

- Features: N/A.

F10/230	RECLAIMED CLAY FACING BRICKWORK WHERE SECOND FLOOR WINDOWS BRICKED UP AT ROOF LEVEL, AND TO ANY REPAIRS/ALTERATIONS TO EXISTING EXTERNAL WALLS

-	Bricks: To match existing.

-	Condition: Sound, free from mortar or deleterious matter.

-	Mortar: As section Z21.

-	Standard: To BS 4721.

-	Mix: 1:1:6 cement:lime:sand.

-	Additional requirements: N/A.

-	Bond: To match existing adjacent.

-	Joints: To match existing adjacent.

-	Features: N/A.

F10/250	140mm CONCRETE FACING BLOCKWORK TO EXPOSED EXTERNAL WALLS AT LOW LEVEL BELOW RENDERED FINISH

-	Blocks: To BS 6073-1.

-	Type: Paint quality, refer to Structural Engineer for strength.

-	Manufacturer: Contractor’s choice.

-	Work sizes (length x height x thickness): 440 x 215 x 140mm.

-	Finish/ colour: Fairfaced.

-	Special shapes: N/A.

-	Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: refer to Structural Engineer’s details.

-	Additional requirements: None.

-	Bond: Stretcher.

-	Joints: Flush.

- Features: Blocks to be laid so that cut ends are built in not exposed.

F10/252	CONCRETE BLOCKWORK TO PLASTERED OR DRYLINED EXTERNAL INTERNAL WALLS

-	Blocks: To BS 6073-1.

-	Type: Standard quality solid aggregate blocks.

-	Manufacturer: Contractor’s choice.

-	Average compressive strength (minimum): refer to Structural Engineer’s details.

-	Work sizes (length x height x thickness): 440 x 215 x width as shown on drawings (140 or 100mm).

-	Finish/ colour: As standard.

-	Special shapes: N/A.

-	Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: 1:1:6 cement:lime:sand above DPC, 1:1/4:3 below DPC.

-	Additional requirements: None.

-	Bond: Stretcher.

-	Joints: Flush.

- Features: None.

F10/253	CONCRETE COMMON BLOCKWORK BELOW GROUND

-	Blocks: To BS 6073-1.

-	Type: Standard quality solid aggregate blocks.

-	Manufacturer: Contractor’s choice.

-	Average compressive strength (minimum): refer to Structural Engineer’s details.

-	Work sizes (length x height x thickness): 440 x 215 x 140mm or 100mm.

-	Finish/ colour: As standard.

-	Special shapes: N/A.

-	Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: refer to Structural Engineer’s details, with sulfate resisting cement		-	Additional requirements: None.

-	Bond: Stretcher.

-	Joints: Flush.

-	Features: None.

F10/315	CLAY COMMON BRICKWORK TO SUB-STATIONS, AS BACKINGS AND BELOW GROUND, AS RECOMMENDED BY EDF

-	Bricks: To BS EN 771-1.

-	Type: Flettons .

-	.Size: 215 x 102 x 65 mm.

-	Mortar: As section Z21.

-	Bond: stretcher in backings, flemish where solid 215 thick wall.

F10/380	ENGINEERING BRICKWORK BELOW DPC

-	Engineering bricks: To BS 3921.

-	Class B.

-	Manufacturer: Contractor’s choice.

Product reference: Blue/grey engineering bricks to Architect’s approval.

-	Mortar: As section Z21.

-	Standard: To BS EN 998-2.

-	Mix: refer to Structural Engineer’s details, with sulfate resisting cement.

-	Additional requirements: None.

-	Bond: Stretcher.

-	Joints: Flush.

WORKMANSHIP GENERALLY

F10/430	CONDITIONING OF CLAY AND CALCIUM SILICATE BRICKS

-	Bricks delivered warm from manufacturing process: Do not use until cold.

-	Absorbent bricks in warm weather: Wet to reduce suction. Do not soak.

F10/440	CONDITIONING OF CONCRETE BRICKS/ BLOCKS

-	Autoclaved concrete bricks/ blocks delivered warm from manufacturing process: Do not use.

-	Age of nonautoclaved concrete bricks/ blocks: Do not use until at least four weeks old.

-	Avoidance of suction in concrete bricks/ blocks: Do not wet.

-	Use of water retaining mortar admixture: Submit details.

F10/500	LAYING GENERALLY

-	Mortar joints: Fill vertical joints. Lay bricks, solid and cellular blocks on a full bed.

-	Bond where not specified: Half lap stretcher.

-	Vertical joints in facework: Even widths. Plumb at every fifth cross joint.

F10/535	HEIGHT OF LIFTS IN WALLING USING CEMENT GAUGED OR HYDRAULIC LIME MORTAR

-	Quoins and advance work: Rack back.

-	Lift height (maximum): 1.2 m above any other part of work at any time.

-	Daily lift height (maximum): 1.5 m for any one leaf.

F10/545	LEVELLING OF SEPARATE LEAVES USING CEMENT GAUGED OR HYDRAULIC LIME MORTAR

-	Locations for equal levelling of cavity wall leaves: As follows:

-	Every course containing vertical twist type ties or other rigid ties.

-	Every third tie course for double triangle/ butterfly ties.

-	Courses in which lintels are to be bedded.

F10/560	COURSING BRICKWORK

-	Gauge: Four brick courses including bed joints to 300 mm.

F10/561	COURSING BRICKWORK WITH EXISTING

-	Gauge: Line up with existing brick courses.

F10/580	LAYING FROGGED BRICKS

-	Single frogged bricks: Frog uppermost.

-	Double frogged bricks: Larger frog uppermost.

-	Frog cavity: Fill with mortar.

F10/610	SUPPORT OF EXISTING WORK

-	Joint above inserted lintel or masonry: Fully consolidated with semidry mortar to support existing structure.

F10/635	JOINTING

-	Profile: Consistent in appearance.

F10/645	ACCESSIBLE JOINTS NOT EXPOSED TO VIEW

- Jointing: Struck flush as work proceeds.

F10/665	POINTING TO ALL NEW BRICKWORK

-	Joint preparation: Remove debris. Dampen surface.

-	Mortar: As section Z21.

-	Standard: TO BS EN 998-2 .

-	Mix: to match bedding mortar .

-	Profile: flush .

F10/690	ADVERSE WEATHER

-	General: Do not use frozen materials or lay on frozen surfaces.

-	Air temperature requirements: Do not lay bricks/ blocks:

-	In cement gauged mortars when at or below 3°C and falling or unless it is at least 1°C and rising.

-	In hydraulic lime:sand mortars when at or below 5°C and falling or below 3°C and rising.

-	In thin joint mortar glue when outside the limits set by the mortar manufacturer.

-	Temperature of walling during curing: Above freezing until hardened.

-	Newly erected walling: Protect at all times from:

-	Rain and snow.

-	Drying out too rapidly in hot conditions and in drying winds.

ADDITIONAL REQUIREMENTS FOR FACEWORK

F10/710	THE TERM FACEWORK

-	Definition: Applicable in this specification to all brick/ block walling finished fair.

-	Painted facework: The only requirement to be waived is that relating to colour.

F10/740	FINISHED MASONRY WORK REFERENCE PANELS

-	General: Before proceeding to construct the following walling types, construct panels as specified. Give notice when panels are dry.

-	Selection of masonry units: Reasonably representative of the average quality of the whole order to be delivered.

-	Panel type A:

-	Walling type: F10/110 and F10/380.

Location: To be agreed.

Size: 1500 x 1500mm.

Other requirements: Weepvent.

-	Panel type B:

-	Walling type: F10/250.

Location: To be agreed.

Size: 1500 x 1500mm.

Other requirements: None.

F10/750	COLOUR CONSISTENCY OF MASONRY UNITS

-	Colour range: Submit proposals of methods taken to ensure that units are of consistent and even appearance within deliveries.

-	Conformity: Check each delivery for consistency of appearance with previous deliveries and with approved reference panels; do not use if variation is excessive.

-	Finished work: Free from patches, horizontal stripes and racking back marks.

F10/760	APPEARANCE

-	Brick/ block selection: Do not use units with damaged faces or arrises.

-	Cut masonry units: Where cut faces or edges are exposed cut with table masonry saw.

-	Quality control: Lay masonry units to match relevant reference panels.

-	Setting out: To produce satisfactory junctions and joints with built-in elements and components.

-	Coursing: Evenly spaced using gauge rods.

-	Lifts: Complete in one operation.

-	Methods of protecting facework: Submit proposals.

F10/780	GROUND LEVEL

-	Commencement of facework: Not less than 150 mm below finished level of adjoining ground or external works level.

F10/790	PUTLOG SCAFFOLDING

-	Use: Not permitted in facework.

F10/830	CLEANLINESS

-	Facework: Keep clean.

-	Mortar on facework: Allow to dry before removing with stiff bristled brush.

-	Removal of marks and stains: Rubbing not permitted.