R12	BELOW GROUND DRAINAGE SYSTEMS

To be read with Preliminaries/ General conditions.

GENERAL

R12/110	BELOW GROUND DRAINAGE SYSTEMS To new extensions and existing buildings.

-	Surface water and rainwater drainage sources: Existing rainwater pipework serving existing buildings, new extensions roofing.

-	Foul drainage sources: New toilet, classroom and admin areas in existing building and new extensions, see drawings.

-	Pipes, bends and junctions: Generally PVCu Plastics

-	Accessories: Access point, rodding points.

-	New P.C.C.manholes, PVCu inspection chambers, traps.

-	Accessories: Ductile iron covers and frames

-	Disposal: Existing foul sewers on site

PRODUCTS

R12/313	ONE PIECE GULLIES RAINWATER PIPEWORK

-	Standards:

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

-	Polypropylene: To BS EN 1852-1.

-	Material: PVCu

-	Manufacturer: Contractors choice .

-	Sizes: To suit

-	Outlet sizes: 110mm.

-	Silt buckets: Required

-	Covers (where applicable): cast iron

R12/315	ONE PIECE GULLIES AND COVERS TO FOUL DRAINAGE

-	Standards:

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

-	Polypropylene: To BS EN 1852-1.

-	Material: PVCu

-	Manufacturer: Contractors choice

-	Sizes: To suit .

-	Outlet sizes: 110mm

-	Covers: Ductile iron or similar .

R12/329	PIPES, BENDS AND JUNCTIONS - SUPPLY

-	Pipes and fittings: From same manufacturer for each pipeline.

.

R12/346	PIPES, BENDS AND JUNCTIONS - PVC-U - PLAIN WALL FOR STORM AND FOUL DRAINAGE

-	Standard: BS EN 1401-1, class SN4, with flexible joints, Kitemark certified.

-	Manufacturer: Osma or equivalent

-	Product reference: Osmadrain

-	Sizes: 110 and 150mm .

-	Application area code: UD.

R12/352	ACCESS POINTS - PLASTICS

-	Standard: To BS 4660 and Kitemark certified, to BS EN 13589-1, or Agrément certified.

-	Manufacturer: Contractors choice .

-	Nominal diameter: 225mm .

-	Bases: As manufacturer’s recommendations

-	Raising pieces: As manufacturer’s recommendations

-	Heights: to suit .

-	Access covers and frames:

-	Loading grades to BS EN 124: A15 for pedestrians .

R12/359	FLEXIBLE COUPLINGS

-	Standard: To BS EN 295-4 or WIS 04-41-01 and Kitemark certified, or Agrément certified.

-	Manufacturer: Osma or equivalent

R12/361	FRESH AIR INLETS TO STUB STACKS- Air admittance valves

- Manufacturer: Contractors choice

R12/371	RODDING POINTS

-	Standards:

-	Cast iron: To BS 437 and Kitemark certified, or Agrément certified.

-	Clay: To BS EN 295-1 and Kitemark certified, or Agrément certified.

-	Concrete: To BS 5911-6 and Kitemark certified, or Agrément certified.

-	Plastics: To BS 4660 and Kitemark certified, or Agrément certified.

-	Material: Plastic .

-	Manufacturer: Contractors choice .

R12/401	INSPECTION CHAMBERS – PLASTICS. PLAYGROUND AREAS, LIGHT TRAFFIC

-	Standard: To BS 7158 or BS EN 13598-1, or Agrément certified.

-	Diameter: 450mm

-	Manufacturer: OSMA

-	Bases:

-	Product reference: Universal Inspection Chamber

-	Access covers and frames:

-	Product reference: Ductile Iron Cover and frame

-	Loading grades to BS EN 124-BB125 Medium Duty

R12/407	MANHOLES AND INSPECTION CHAMBERS – CONCRETE. CAR PARKING AREAS

-	Standards:

-	To BS 5911-3 and BS EN 1917 and Kitemark certified; or

-	To BS 5911-4 and BS EN 1917.

-	Manufacturer: Contractors choice

-	Shape: Circular

-	Sizes: 900 dia. .

-	Cement type and content: Sulfate resisting

-	Cover slabs:

-	Product reference: Contractors choice

-	Thickness: To suit

-	Loading grades to BS EN 124: Heavy Duty .

-	Openings: To suit access covers.

-	Steps: Galvanised @ 300 vert c/c’s .

420	EXTERNAL DRAINAGE CHANNELS – THRESHOLDS & AS DRAWINGS

- 	Material: Pre cast concrete

-	Manufacturer: Aco

-	Product reference: Aco Raindrain channel system N100K, including channels,sump units,foul air traps, closing end caps and lifting tools to suit. Galvanised slotted gratings.

R12/433	MANHOLE CHANNELS AND BRANCHES - CONVENTIONAL

-	Material: Vitrified clay

-	Manufacturer: Hepworth

-	Product reference: Supasleve

R12/435	MANHOLE CHANNELS AND BRANCHES - PREFORMED PLASTICS

-	Manufacturer: Osma.

-	Product reference: Inspection Chamber Base

R12/446	SEALING FOR CONCRETE MANHOLES - MORTAR

-	Manufacturer: Contractors choice.

R12/471	ACCESS COVERS AND FRAMES  TO ALL INSPECTION CHAMBERS/MANHOLES

-	Standard: To BS EN 124.

-	Types: Single seal, recessed for resin bound gravel paving at front entrance areas and in nursery playground

-	Manufacturer: Contractors choice

-	Materials: Ductile Iron.

-	Finishes: Hot dip galvanised.

-	Sizes: To suit

-	Loading grades to BS EN 124: B125(PVCu Inspection Chambers) C250 (PCC)

R12/483	CONCRETE (GENERAL)

-	Standards: To BS 8500-1, -2 and BS EN 206-1.

-	Concrete: GEN1

R12/485	CONCRETE (STRUCTURAL)

-	Standards: To BS 8500-1, -2 and BS EN 206-1.

-	Concrete: GEN3

R12/496	GRANULAR MATERIAL

-	Standard: To BS EN 12620.

-	Size: Dependent on location - see Execution clauses in this section, and in sections R16, R17 and R18.

R12/498	GRANULAR SUB-BASE MATERIAL

-	Standard: To Highways Agency Volume 1, ‘Specification for Highway Works’, Type 1 Unbound mixtures for sub-base.

EXECUTION

R12/610	STRIPPING OUT

-	Extent of stripping out: Redundant underground foul and surface water drain runs- see drawings

-	Exposed ends of existing drainage to be abandoned: Seal with concrete (general).

R12/611	EXISTING DRAINS

-	Setting out: Before starting work, check invert levels and positions of existing drains, sewers, inspection chambers and manholes against drawings. Report discrepancies.

-	Protection: Protect existing drains to be retained and maintain normal operation if in use.

R12/613	EXCAVATED MATERIAL

-	Turf, topsoil, hardcore, etc: Set aside for use in reinstatement.

R12/616	SELECTED FILL FOR BACKFILLING

-	Selected fill: As-dug material, free from vegetable matter, rubbish, frozen soil and material retained on a 40 mm sieve.

-	Compaction: By hand in 100 mm layers.

R12/623	LOWER PART OF TRENCH - GENERAL

-	Trench up to 300 mm above crown of pipe: Vertical sides, width as small as practicable.

-	Width (minimum): External diameter of pipe plus 300 mm.

R12/631	TYPE OF SUBSOIL

-	General: Where type of subsoil at level of crown of pipe differs from that stated for the type of bedding, surround or support, give notice.

R12/635	FORMATION FOR BEDDINGS

-	Timing: Excavate to formation immediately before laying beddings or pipes.

-	Mud, rock projections, boulders and hard spots: Remove. Replace with consolidated bedding material.

-	Local soft spots: Harden by tamping in bedding material.

-	Inspection of excavated formations: Give notice.

R12/663	CLASS P SUPPORT FOR PVCu PIPEWORK NOT UNDER BUILDINGS

-	Type of subsoil: See soil report

-	Granular material:

-	Pipe sizes DN 100 and DN 150: Size 4/10.

-	Pipe sizes DN 225 and DN 300: Size 4/10, 10/20 or 4/20.

-	Bedding:

-	Material: Granular, compacted over full width of trench.

-	Thickness (minimum): 100 mm.

-	Pipes: Dig slightly into bedding, rest uniformly on barrels and adjust to line and gradient.

-	Initial testing before placing support: Required

-	Support:

-	Material: Granular.

-	Depth: To slightly above crown of pipe.

-	Compaction: By hand.

-	Backfilling:

-	Material and depth:

Protective cushion of selected fill to 300 mm above crown of pipe; or

Additional granular material, to 100 mm above crown of pipe.

-	Compaction: By hand in 100 mm layers.

R12/665	CLASS Q SURROUND FOR PIPEWORK NOT UNDER BUILDINGS

-	Type of subsoil: See soil report

-	Granular material:

-	Pipe sizes DN 100 and DN 150: Size 4/10.

-	Pipe sizes DN 225 and DN 300: Size 4/10, 10/20 or 4/20.

-	Bedding:

-	Material: Granular, compacted over full width of trench.

-	Thickness (minimum): 100 mm.

-	Pipes: Dig slightly into bedding, rest uniformly on barrels and adjust to line and gradient.

-	Initial testing before placing support: Required

-	Surround:

-	Material: Granular.

-	Depth (minimum): To 75 mm above crown of pipe.

-	Compaction: By hand.

-	Protection slabs:

-	Material: Pre-cast concrete to BS7263-1

-	Thickness: 50mm

-	Minimum bearing: 300 mm.

-	Backfilling: Soil or topsoil, as appropriate.

R12/673	CLASS W SURROUND FOR PIPEWORK UNDER BUILDINGS.

-	Type of subsoil: See soil report .

-	Granular material:

-	Pipe sizes DN 100 and DN 150: Size 4/10.

-	Pipe sizes DN 225 and DN 300: Size 4/10 or 10/20.

-	Bedding:

-	Material: Granular, compacted over full width of trench.

-	Thickness (minimum): 100 mm.

-	Pipes: Dig slightly into bedding, rest uniformly on barrels and adjust to line and gradient.

-	Initial testing before placing surround: Required

-	Surround:

-	Material: Granular.

-	Depth: To 100 mm above crown of pipe.

-	Compaction: By hand.

-	Backfilling:

-	Material: Hardcore as section D20, or granular.

-	Depth: Up to ground level formation .

-	Compaction: In 300 mm (maximum) thick layers.

R12/680	CONCRETE SURROUND FOR PIPE RUNS NEAR FOUNDATIONS

-	Class Z surround: Provide in locations where bottom of trench is lower than bottom of foundation and as follows (horizontal clear distance between nearest edges of foundations and pipe trenches):

-	Trenches less than 1 m from foundations: Top of concrete surround not lower than bottom of foundation.

-	Trenches more than 1 m from foundations: Top of concrete surround not lower than D mm below bottom of foundation, where D mm is horizontal distance of trench from foundation, less 150 mm.

R12/683	LAYING PIPELINES

-	Laying pipes: To true line and regular gradient on even bed for full length of barrel with sockets (if any) facing up the gradient.

-	Ingress of debris: Seal exposed ends during construction.

-	Timing: Minimize time between laying and testing.

R12/685	JOINTING PIPELINES

-	Connections: Durable, effective and free from leakage.

-	Junctions, including to differing pipework systems: With adaptors intended for the purpose.

-	Cut ends of pipes: Clean and square. Remove burrs and swarf. Chamfer pipe ends before inserting into ring seal sockets.

-	Jointing or mating surfaces: Clean and, where necessary, lubricate immediately before assembly.

-	Allowance for movement: Provide and maintain appropriate clearance at ends of spigots as fixing and jointing proceeds.

-	Jointing material: Do not allow to project into bore of pipes and fittings.

R12/689	PIPELINES PASSING THROUGH STRUCTURES

-	Pipelines that must be cast in or fixed to structures (including manholes, catchpits and inspection chambers): Provide 600 mm long rocker pipes adjacent to the external face of the structure (or both faces where appropriate, e.g. walls to footings), with flexible joints at both ends.

-	Distance to rocker pipe from structure (maximum):150 mm.

-	Provision for movement for pipelines that need not be cast in or fixed to structures (e.g. walls to footings):

-	Rocker pipes as specified above; or

-	Openings in the structures to give 50 mm minimum clearance around the pipeline. Closely fit a rigid sheet to each side of opening to prevent ingress of fill or vermin.

R12/691	BENDS AT BASE OF SOIL STACKS

-	Type: Nominal rest bends .

-	Radius to centreline of pipe (minimum): 200mm.

-	Height of invert of horizontal drain at base of stack below centreline of lowest branch pipe (minimum): 450mm

-	Bedding: Do not impair flexibility of pipe couplings.

-	Material: Concrete (general).

R12/693	DIRECT CONNECTION OF GROUND FLOOR WCS TO DRAINS

-	Drop from crown of WC trap to invert of drain (maximum):1.3m max..

-	Horizontal distance from the drop to a ventilated drain (maximum): 6 m.

R12/697	INSTALLING FLEXIBLE COUPLINGS

-	Ends of pipes to be joined: Cut cleanly and square.

-	Outer surfaces of pipes to be joined: Clean and smooth. Where necessary, e.g. on concrete or iron pipes, smooth out mould lines and/ or apply a cement grout over the sealing area.

-	Clamping bands: Tighten carefully to make gastight and watertight seals.

R12/705	INITIAL TESTING OF PIPELINES

-	Before testing:

-	Cement mortar jointing: Leave 24 h.

-	Solvent welded pipelines: Leave 1 h.

-	Method: Block open ends of pipelines to be tested and pressurise. Air test short lengths to BS EN 1610.

R12/715	BACKFILLING TO PIPELINES

-	Backfilling above top of surround or protective cushion: Material excavated from trench, compacted in layers 300 mm (maximum) thick.

-	Heavy compactors: Do not use before there is 600 mm (total) of material over pipes.

R12/720	BACKFILLING UNDER ROADS AND PAVINGS

-	Backfilling from top of surround or protective cushion up to formation level: Granular sub-base material, laid and compacted in 150 mm layers.

R12/722	PUBLIC ROADS AND PAVINGS - E & W, SCOT

-	Excavating and backfilling of trenches: To Department for Transport ‘Specification for the reinstatement of openings in highways’.

R12/724	PUBLIC ROADS AND PAVINGS - NI

-	Excavating and backfilling of trenches: To Northern Ireland Road Authority and Utilities Committee ‘Specification for the reinstatement of openings in highways’.

R12/728	LAYING WARNING MARKER TAPES

-	Installation: During backfilling, lay continuously over pipelines.

-	Depth: 300-400 mm.

-	Pipelines deeper than 2 m: Lay an additional tape 600 mm above the top of the pipeline.

R12/734	INSTALLING GULLIES

-	Bedding:

-	Material: Concrete GEN1

-	Thickness (minimum): 150mm .

-	Surround:

-	Material: Concrete GEN1

-	Thickness (minimum): 150mm.

-	Permissible deviation in level of external covers and gratings: +0 to -6 mm.

-	Raising pieces (clay and concrete units): Joint with 1:3 cement:sand mortar.

-	Exposed openings: Fit purpose made temporary caps. Protect from site traffic.

R12/741	INSTALLING INSPECTION CHAMBERS - PLASTICS

-	Bedding:

-	Material: Concrete GEN 1

-   Thickness (minimum): 150mm

-	Surround

-    Material: Concrete GEN 1 .

-	Thickness (minimum): 100mm .

-     Backfilling: Not required

-	Concrete collar:

-	Material: Concrete GEN1

-	Thickness (minimum): 100mm .

-    Width (minimum): As recommended by Manufacturer

R12/743	INSTALLING CONCRETE MANHOLES

-	Bases:

-	Material: Concrete GEN 2

-	Thickness (minimum): 225mm .

-	Surround:

-	Material: Not required

-	Backfilling:

-	Material: Concrete GEN 1

-	Thickness: 100mm min.

R12/753	FIXING MANHOLE STEPS

-	Fixing: Bed in joints.

-	Positioning: 300 mm vertical centres staggered 300 mm horizontally, with lowest step 300 mm (maximum) above benching and top step 450 mm (maximum) below top of cover.

R12/755	JOINTING CONCRETE MANHOLE CHAMBER SECTIONS

-	Jointing and sealing: Mortar

-	Inner joint surface: Trim surplus jointing material extruded into chamber and point neatly.

R12/757	LAYING CONVENTIONAL CHANNELS, BRANCHES AND BENCHING

-	Main channel: Bed solid in 1:3 cement:sand mortar.

-	Branches: Connect to channel, preferably at half pipe level, so that discharge flows smoothly in direction of main flow.

-	Branches greater than nominal size 150 mm: Connect the branch soffit level with the main drain soffit.

-	Connecting angles more than 45° to direction of flow: Use three-quarter section channel bends.

-	Benching:

-	Material: Concrete GEN 1

-	Profile: Rise vertically from top of main channel to a level not lower than soffit of outlet pipe, then slope upwards at 10% to walls.

-	Topping:

Material: Cement:sand mortar 1:3

Application: Before benching concrete has set, and with dense smooth uniform finish.

R12/759	LAYING PREFORMED PLASTICS CHANNELS, BRANCHES AND BENCHING

-	Main channel: Bed solid in 1:3 cement:sand mortar.

-	Branches: Connect to channel, preferably at half pipe level, so that discharge flows smoothly in direction of main flow.

-	Connecting angles more than 45° to direction of flow: Use three-quarter section channel bends.

-	Bedding: 1:3 cement:sand mortar. Use clips or ensure adequate mechanical key.

-	Benching:

-	Material: Concrete (general).

-	Profile: Rise vertically from top of main channel to a level not lower than soffit of outlet pipe, then slope upwards at 10% to walls.

-	Topping:

Material: Cement:sand mortar 1:3

Application: Before benching concrete has set, and with dense smooth uniform finish.

R12/773	INSTALLING ACCESS COVERS AND FRAMES

-	Seating: Concrete or brick.

-	Bedding and haunching of frames: Continuously.

-	Material: Cement:sand mortar 1:3

-	Top of haunching: 30 mm below surrounding surfaces.

-	Horizontal positioning of frames:

-	Centred over openings.

-	Square with joints in surrounding paving.

-	Vertical positioning of frames:

-	Level; or

-	Marry in with levels of surrounding paving.

-	Permissible deviation in level of external covers and frames: +0 to -6 mm.

R12/776	EXPOSED OPENINGS IN INSPECTION CHAMBERS, ACCESS POINTS, FITTINGS AND EQUIPMENT

-	General: Fit purpose made temporary caps. Protect from site traffic.

COMPLETION

R12/901	REMOVAL OF DEBRIS AND CLEANING

-	Preparation: Lift covers to manholes, inspection chambers and access points. Remove mortar droppings, debris and loose wrappings.

-	Timing: Before cleaning, final testing, CCTV inspection if specified, and immediately before handover.

-	Cleaning: Thoroughly flush pipelines with water to remove silt and check for blockages. Rod pipelines between access points if there is any indication that they may be obstructed.

-	Washings and detritus: Do not discharge into sewers or watercourses.

-	Covers: Securely replace after cleaning and testing.

R12/903	TEMPORARY MEASURES

-	Water used to stabilize tanks and the like during installation: Drain.

R12/911	TESTING AND INSPECTION

-	Dates for testing and inspection: Give notice.

-	Period of notice: 72 hours.

R12/921	FINAL TESTING OF PRIVATE GRAVITY DRAINS AND SEWERS UP TO DN 300

-	Before testing:

-	Cement mortar jointing: Leave 24 h.

-	Solvent welded pipelines: Leave 1 h.

-	Standard: To Building Regulations.

-	Method: Contractors choice

R12/941	WATER TESTING OF MANHOLES AND INSPECTION CHAMBERS

-	Timing: Before backfilling.

-	Standard:

-	Exfiltration: To BS EN 1610.

Method: Testing with water (method W).

-	Infiltration: No identifiable flow of water penetrating the chamber.