R10	RAINWATER DRAINAGE SYSTEMS

To be read with Preliminaries/ General conditions.

GENERAL

R10/110	GRAVITY RAINWATER DRAINAGE SYSTEM

-	Rainwater outlets: Proprietary .

-	Gutters: Aluminium .

-	Pipework: Aluminium where exposed, cast iron where concealed .

-	Below ground drainage: As section R12 .

-	Disposal: As section R12 .

SYSTEM PERFORMANCE

R10/210	DESIGN

-	Design: Complete the design of the rainwater drainage system.

-	Standard: To BS EN 12056-3, clauses 3–7 and National Annexes.

-	Proposals: Submit drawings, technical information, calculations and manufacturers’ literature.

R10/221	COLLECTION AND DISTRIBUTION OF RAINWATER

-	General: Complete, and without leakage or noise nuisance.

R10/230	DESIGN PARAMETERS – GENERAL

-	Roof and gutter construction and finish: see drawings .

-	Design rate of rainfall: As BS EN 12056-3, National Annex NB.2.

-	Design life of building: 40 years .

-	Available capacity of existing below ground drainage (maximum): to be checked .

PRODUCTS

R10/311	ALUMINIUM GUTTERS

-	Standard: To BS2997 .

-	Manufacturer: Aluminium Roofline Products or equal approved .

-	Product reference: Legion pressed box gutters .

-	Profile: see drawings .

-	Type/ Thickness: cast .

-	Nominal size: 150 x 100 for sub-station and bike store, 200 x 150 elsewhere .

-	Finish: mill finish to nursery canopy, polyester powder coated elsewhere .

-	Colour: to be agreed .

-	Brackets: Manufacturer’s recommended type .

-	Fixings: Manufacturer’s recommended type .

-	Accessories: Running outlets, stop ends and angles, brackets .

R10/360	SEALANT FOR GUTTERS

-	Type: To manufacturer;s recommnedation .

R10/365A	PROPRIETARY RAINWATER OUTLETS

-	Manufacturer: Wade

-	Product reference: 100mm Roof outlet see detail drawings,

-	Roof construction: See detail drawings

-	Roof insulation thickness: See details

-	Type of grate/ Fittings: Raising pieces to accommodate the roof insulation if necessary.

-	Outlet: Type and direction to suit pipework with suitable adaptors and connections.

-	Accessories: As recommended by manufacturer .

R10/365B	PROPRIETARY RAINWATER HOPPER

-	Manufacturer: Aluminium Roofline Products or equal approved

-	Product reference: Polyester powder coated Juno Colonnade cast aluminium hopper

-	Outlet: Type, size and direction to suit pipework with suitable adaptors and connections.

-	Accessories: As recommended by manufacturer .

R10/370	ALUMINIUM PIPEWORK

-	Standard: To BS 2997.

-	Manufacturer: Aluminium Roofline Products or equal approved .

-	Type/ Thickness : Sheet, 1.22mm .

-	Section: Circular.

-	Nominal size: 76mm for playcentre extension, bike store and sub-station, 100mmm diameter elsewhere.

-	Finish: Mill finish to nursery canopy, polyester powder coated elsewhere.

-	Brackets: As manufacturer’s recommendations.

-	Accessories: Rainwater shoes .

R10/375	CAST IRON PIPEWORK – FLEXIBLE COUPLINGS

-	Standard: To BS EN 877, Agrément certified.

-	Manufacturer: Contractor’s choice .

-	Coupling type: As manufacturer’s recommendations .

-	Nominal size: 100mm .

-	Finish as supplied: As manufacturer’s recommendations .

-	Brackets: As manufacturer’s recommendations .

R10/450	INSULATION TO INTERNAL PIPELINES

-	Material: Pre-formed closed cell split tube .

-	Thermal conductivity (maximum): 0.045W/mK .

-	Manufacturer: Contractor’s choice .

-	Fire performance: Class 1 spread of flame when tested to BS 476-7 or Class C to BS EN 13501 .

EXECUTION

R10/600	PREPARATION

-	Work to be completed before commencing work specified in this section:

-	Below ground drainage. Alternatively, make temporary arrangements for dispersal of rainwater without damage or disfigurement of the building fabric and surroundings.

-	Painting of surfaces which will be concealed or inaccessible.

R10/605	INSTALLATION GENERALLY

-	Electrolytic corrosion: Avoid contact between dissimilar metals where corrosion may occur.

-	Plastics and galvanized steel pipes: Do not bend.

-	Allowance for thermal and building movement: Provide and maintain clearance as fixing and jointing proceeds.

-	Protection:

-	Fit purpose made temporary caps to prevent ingress of debris.

-	Fit access covers, cleaning eyes and blanking plates as the work proceeds.

610	FIXING AND JOINTING GUTTERS

•	 Joints: Watertight  	.

•	 Brackets: Securely fixed.

-	Fixings: self-tapping screws to purlins .

Fixing centres: as manufacturers recommendations .

- Additional brackets: Where necessary to maintain support and stability, provide

at joints in gutters and near angles and outlets.

•	 Roofing underlay: Dressed into gutter.

R10/616	SETTING OUT EAVES GUTTERS – LEVEL

-	Setting out: Level and as close as practical to the roof.

-	Outlets: Aligned with connections to below ground drainage.

R10/630	INSTALLING RAINWATER OUTLETS

-	Fixing: Secure. Fix before connecting pipework.

-	Method: Grout into preformed holes .

-	Junctions between outlets and pipework: Accommodate movement in structure and pipework.

R10/635	FIXING PIPEWORK

-	Pipework: Fix securely, plumb and/ or true to line.

-	Branches and low gradient sections: Fix with uniform and adequate falls to drain efficiently.

-	Externally socketed pipes and fittings: Fix with sockets facing upstream.

-	Additional supports: Provide as necessary to support junctions and changes in direction.

-	Provide a loadbearing support at least at every storey level.

-	Tighten fixings as work proceeds so that every storey is self supporting.

-	Wedge joints in unsealed metal pipes to prevent rattling.

-	Wall and floor penetrations: Isolate pipework from structure.

-	Pipe sleeves: As section P31.

-	Masking plates: Fix at penetrations if visible in the finished work.

-	Expansion joint pipe sockets: Fix rigidly to buildings. Elsewhere, provide brackets and fixings that allow pipes to slide.

R10/640	FIXING VERTICAL PIPEWORK

-	Bracket fixings: fix securely, plumb and/or true to line .

-	Distance between bracket fixing centres (maximum): As manufacturer’s recommendations .

R10/650	JOINTING PIPEWORK AND GUTTERS

-	General: Joint with materials and fittings that will make effective and durable connections.

-	Jointing differing pipework and gutter systems: Use adaptors intended for the purpose.

-	Cut ends of pipes and gutters: Clean and square. Remove burrs and swarf. Chamfer pipe ends before inserting into ring seal sockets.

-	Jointing or mating surfaces: Clean and, where necessary, lubricate immediately before assembly.

-	Junctions: Form with fittings intended for the purpose.

-	Jointing material: Strike off flush. Do not allow it to project into bore of pipes and fittings.

-	Surplus flux, solvent jointing materials and cement: Remove.

R10/655	JOINTING INTERNAL PIPEWORK

-	Jointing: As manufacturer’s recommendations .

R10/660	JOINTING EXTERNAL PIPEWORK

-	Jointing: As manufacturer’s recommendations .

R10/675	CUTTING COATED PIPEWORK AND GUTTERS

-	Cutting: Recoat bare metal.

R10/680	FIXING INSULATION TO INTERNAL PIPELINES AND GUTTERS

-	Fixing: Secure and neat. Provide continuity at supports and leave no gaps. Fix split pipe insulation with the split on ‘blind’ side of pipeline.

-	Timing: Do not fit insulation until completion of pipe airtightness or leakage testing.

COMPLETION

R10/905	INTERNAL PIPEWORK TEST – ENGLAND, WALES, IRELAND AND NORTHERN IRELAND

-	Preparation: Temporarily seal open ends of pipework with plugs.

-	Test apparatus: Connect a ‘U’ tube water gauge and air pump to pipework via a plug.

-	Testing: Pump air into pipework until gauge registers 38 mm.

-	Required performance:

-	Allow a period for temperature stabilization, after which the pressure of 38 mm is to be maintained without loss for at least 3 minutes.

R10/910	GUTTER TEST

-	Preparation: Temporarily block all outlets.

-	Testing: Fill gutters to overflow level and after 5 minutes closely inspect for leakage.