N25	PERMANENT ACCESS AND SAFETY EQUIPMENT

To be read with Preliminaries/ General conditions.

TYPES OF SYSTEM/ EQUIPMENT

N25/210	GUIDED TYPE FALL ARREST SYSTEM FOR ROOF MAINTENANCE AND ACCESS TO ALL NEW ROOFS OF NEW EXTENSIONS

-	Manufacturer: Contractor’s choice to PIFA standard 6/83A or Agrément certified.

-	Anchorage device: Horizontal stainless steel cable.

-	Overall system length: As necessary for safe access to all parts of roof.

-	Intermediate support spacing: In accordance with system manufacturer’s recommendations.

-	Installation: To BS 7883 by the system manufacturer or a contractor approved by the system manufacturer.

-	Structural anchors: Type recommended by the system manufacturer to suit the structure/ fabric into which they will be fixed.

DESIGN/ PERFORMANCE REQUIREMENTS

410     WIND LOADING

- General: Design access/ safety system to withstand calculated wind loads with

- equipment in position of maximum exposure and in parked position.

-     Wind loads: Calculate in accordance with BS 6399-2, Standard Method:

-        Basic wind speed (Vb): 21 m/s .

-        Altitude factor (Sa): 1.1.

-        Direction factor (Sd): 1.

-        Seasonal factor (Ss): 1.

-        Probability factor (Sp): 1.

-        Terrain and building factor (Sb), determined from BS 6399-2, table 4: 1.54.

N25/430	SAFETY

-	General: The equipment as installed must have no irregularities/ projections capable of inflicting personal injury.

-	Finished surfaces and edges of all accessible parts: Regular and smooth.

N25/440	DESIGN LIFE/ MAINTENANCE PROGRAMME

-	Design life of access/ safety system: Not less than 20 years.

-	Schedule for maintenance and for replacement of components: Submit.

FABRICATION, ASSEMBLY AND INSTALLATION

N25/510	FABRICATION AND ASSEMBLY GENERALLY

-	Machine cutting, drilling and assembly: Carry out as much as possible in the workshop. Obtain approval for any reassembly on site.

-	Dissimilar metal surfaces of assembly components/ supports/ fixings: Isolate to prevent electrolytic corrosion.

N25/520	PROTECTION

- General: Do not deliver to site any components or assemblies that cannot be installed immediately or unloaded into a suitable well protected storage area.

N25/540	MECHANICAL FIXINGS

-	Materials: Unless otherwise recommended by equipment manufacturer:

-	Connecting bolts and other fixings fully accessible for inspection: Mild steel hot dip galvanized to BS 7371-6.

Nuts: Tapped after galvanizing.

-	Cast-in anchors and other fixings not accessible for routine inspection: Austenitic stainless steel, grade 1.4401 (316) to BS EN 10088-1.

N25/550	FASTENERS, INSERTS AND BOLTS FOR BUILDING IN

-	Supplier: Equipment manufacturer/ supplier.

N25/560	FIXINGS FOR SECURING EQUIPMENT

-	Adjustment capability: Adequate three dimensional adjustment to accommodate building structure/ fabric irregularities.

N25/570	FIXING ANCHOR INSTALLATION

-	Site drilling or cutting into structure/ fabric: Permitted only in approved locations.

-	Distance between all fixing devices and edges of supporting material: Not less than recommended by fixing manufacturer.

N25/640	MARKING OF ANCHOR DEVICES

-	Provision: Provide on or near each anchor device a label or other clear marking giving:

-	Manufacturer’s name and telephone number.

-	Serial number and year of manufacture of device.

-	Maximum number of personnel that may be attached to the device at any one time.

-	Requirements for energy absorbers, ground clearance, etc.

-	Anchor devices intended solely for use with personal protective equipment: Indicate restriction of use by pictogram or other suitable marking on or near the device.

N25/810	SERVICE/ MAINTENANCE OF FALL ARREST SYSTEM

-	General: Following acceptance of the completed installation, service and maintain the equipment for the period stated below as and at intervals recommended by the manufacturer. Such maintenance to include a ‘call-out’ service during normal working hours to maintain the equipment in an acceptable and safe condition.

-	Service/ Maintenance period: 12 months.

N25/820	OPERATING INSTRUCTIONS

-	Equipment and accessories: Where appropriate, mark in such a way that it is possible to identify the correct mode of operation for their safe use.

N25/830	OPERATING AND MAINTENANCE MANUAL

-	General: Provide, for inclusion in the Building Manual, printed instructions and recommended procedures to be established by the Employer for operating and routinely maintaining the equipment. Provide diagrams where appropriate.

-	Content:

-	Instructions for assembling/ erecting equipment for use.

-	Comprehensive operating instructions, including safety and emergency procedures, for all motions including upward, downward and lateral travel, and slew.

-	Servicing and planned maintenance procedures, including assembly instructions where maintenance necessitates dismantling of machinery parts.

-	List of replacement parts, with references.

-	Recommended procedures for testing equipment.