P12	FIRE STOPPING SYSTEMS

To be read with Preliminaries/ General conditions.

GENERAL

P12/130	FIRE STOPPING TO SERVICE PIPES PASSING THROUGH FLOORS AND WALLS

-	Joint filler: Proprietary intumescent mortar to Contractor’s choice (Sealmaster FR or similar approved).

- Pipe outside diameter: Varies.

- Fire resistance: 1 hour

-	Sealant: Contractor’s choice.

P12/160	INTERNAL FIRE RESISTING MOVEMENT JOINTS BETWEEN BLOCKWORK WALLS AND STEEL STRUCTURE

-	Joint preparation and filler application: As section Z22.

-	Filler: closed cell polyethylene.

-	Thickness: To match design width of joint.

-	Manufacturer: Grace Building Products Ltd. or similar approved.

Product reference: 12mm Aerofil.

-	Placement: Build in as work proceeds with no projections into cavities and to correct depth to receive sealant system.

-	Fire resistant filler: Proprietary fire rated acrylic impregnated foam elastic weatherseal to Contractor’s choice (Rockwool Corofil Intumescent Movement Joint or similar approved).

-	Joint width or height (minimum): 12mm.

-	Fire resistance: 1 hour min.

-	Placement: Compress and insert into place in open joint.

-	Adhesives and accessories: Types recommended by filler manufacturer

-	Sealant: Not required.

PRODUCTS

P12/305	PRODUCT CERTIFICATION

-	Certification: For products specified generically, submit evidence of compliance with the specification.

-	Acceptable evidence: Agrément certificate.

EXECUTION

P12/620	WORKMANSHIP GENERALLY

-	Gaps: Seal gaps between building elements and services, to provide fire resistance and resist the passage of smoke.

-	Adjacent surfaces: Prevent overrun of sealant or mortar on to finished surfaces.

P12/660	APPLYING INTUMESCENT MORTAR

-	Sequence: Install mortar after services are permanently installed.

-	Loose dust and combustible materials: Remove from the opening.

-	Shuttering: Install suitable shuttering panels to the faces of the opening.

-	Temperature: Do not apply mortar when it could be damaged by frost.

-	Powder:water ratio: Strictly in accordance with manufacturer’s recommendations.

-	Mortar cure: Do not disturb mortar before final set has taken place.

- Shuttering: Remove after mortar has cured.

661	APPLYING FIRE RESISTANT FOAM ELASTIC WEATHERSEAL

- Sequence: Construct blockwork with suitable compressible board against steel columns and beams.

-	Debris and mortar residue: Remove from the opening.

- Size foam according to manufacturer’s recommendations to suit joint width.

- Form joints in accordance with manufacturer’s recommendations to ensure complete seal around blockwork panels.

COMPLETION

P12/910	CLEANING

-	Masking tapes: Remove.

-	Cleaning: Clean off splashes and droppings. Wipe down finishes.

P12/920	INSPECTION

-	Notice for inspection (minimum): 5 days.