L20	DOORS/ SHUTTERS/ HATCHES

To be read with Preliminaries/ General conditions.

GENERAL

L20/110	EVIDENCE OF PERFORMANCE

-	Certification: Provide independently certified evidence that all incorporated components comply with specified performance requirements.

L20/115	FIRE RESISTING AND ACOUSTIC DOORS/ DOORSETS/ ASSEMBLIES

-	Evidence of fire and acoustic performance: Provide certified evidence, in the form of a product conformity certificate, directly relevant fire and acoustic test report or engineering assessment, that each door/ doorset/ assembly supplied will comply with the specified requirements for fire resistance and acoustic performance if tested to BS 476-22, BS EN 1634-1 or BS EN 1634-3. Such certification must cover door and frame materials, glass and glazing materials and their installation, essential and ancillary ironmongery, hinges and seals.

L20/150	SITE DIMENSIONS

- Procedure: Before starting work on designated items take site dimensions, record on shop drawings and use to ensure accurate fabrication.

- Designited items: all doors in existing openings, and as indicated for site measurement.

PRODUCTS

L20/230	WOOD FLUSH DOORS GENERALLY NON FIRE RESISTING

-	Manufacturer: Contractors choice

-	Facings: Suitable to receive paint finish.

-	Lippings: Hardwood to all edges

-	Finish as delivered: Primed.

-	Glazing details: See drawings.

-	Other requirements: Min. mass 27kg/m2, Acoustic seals(including thresholds) as schedules/drawings

L20/230	WOOD FLUSH DOORS & FRAMES GENERALLY FD30S FIRE RESISTING, INCLUDING GLAZED PANELS

-	Manufacturer: Contractors choice

-	Facings: Suitable to receive paint finish.

-	Lippings: Hardwood to all edges

-	Finish as delivered: Primed.

-	Glazing details: See drawings.  Generally Pilkington Pyradur 10mm

-	Other requirements: Min. mass 27kg/m2. Acoustic and fire/smoke seals as drawings.

275     PURPOSE MADE WOOD EXTERNAL DOORS & FRAMES (PART OF COMBINED DOOR/SCREEN ASSEMBLY)

-	Standard: To BS 644.

-	Manufacturer: A firm currently registered under a third party quality assurance scheme.

-	Operation and strength characteristics: To BS 6375-2.

-	Timber: Generally to BS EN 942.

-	Species: Contractors choice

-	Appearance class: J10 for glazing beads, drip mouldings and the like. J40 or better for all other members.

-	Moisture content on delivery: 12-19%.

-	Preservative treatment: Organic solvent .

-	Finish as delivered: Primed

-	Glazing details: To achieve U value of max. 2.2 W/sqmK. Profiled fixing beads, see details

-	Ironmongery/ Accessories: As schedule

-	Fixing: Galvanised cramps.

L20/315	WOOD DOOR FRAMES/ LININGS INTERNAL

-	Manufacturer: Contractors choice

-	Species: Contractors choice .

-	Preservative treatment: Organic solvent

-	Finish as delivered: Primed

-	Perimeter seals: Acoustic and fire/smoke seals as drawings/schedules.

-	Fixing: Countersunk and pelleted screw fixing, plugged.

330	VELFAC 500 SERIES DOORS DG14A/B & DG14C/D

Manufacturer:

- 	VELFAC Ltd, The Old Livery, Hildersham, Cambridge, CB1 6DR Telephone 01223 897100 Fax 01223 897101

Email ijo@VELFAC.co.uk

Contact – Iain Jones 07825 059 149

Product reference:

Thermally broken rebated doors as fabricated by VELFAC

Materials:

Material Constructed with profiles extruded in anodising grade aluminium AL Mg Si 0.5 F22.

Finish:

The door profiles must be polyester powder-coated in compliance with BS 6496, BS 6497, GSB and DIN 50939, in RAL colour (code TBC) to gloss level 77% and a primary coating thickness of between 60-120 µm

# Thermal Isolator:

The door profiles shall incorporate a rigid polythermide isolator mechanically retained in position, (bonded or foam filled isolators will not be acceptable).  The isolator will afford a level table between the inner and outer profiles.

# Glazing Method:

The doors shall be of the gasket and internal glazing type.  The glazing beads shall be mechanically retained within the window profile and utilise integral glazing clips to ease fitting and removal.

# Glazing Gasketry:

The outer glazing gasket shall be of one length jointed at the head and bonded under compression.  The outer gasket shall be so designed to resist ingress of water into the system, due to the pumping action of wind upon the glass.

The system is to incorporate closed cell gaskets extruded or moulded to BS 4255 Part 2 or DIN 7863.  Inner rebate gaskets shall be formed with a continuous wedge gasket and bonding gasket shall occur at the head of the element.

The sub-contractor shall ensure the alignment of gaskets, in all visible locations.

Gaskets and associated materials are to be free from contact and migration stain characteristics.

# Glass Support:

Glass support blocks are to be designed to self lock into the glazing rebate locations.

# Construction:

The aluminium system shall be mechanically held in position by the use of internal extruded aluminium multi-chambered cleats, and so profiled to accept an injected adhesive.

The corners of the aluminium system shall be mechanically held in position with cleats as so specified and crimped.

The corners of the aluminium system shall be mechanically held in position with cleats as so specified and nailed.

The mitres formed within the inner rebate areas are to be stabilised by the insertion of stainless steel spring chevrons.

Mitres formed during the construction of the framing elements are to be epoxy bonded.

# Ironmongery/Accessories:

Doors within this sub-contract shall operate and be handed as designated on the architects drawings.

Handles - Full height handles made from 38mm diameter stainless steel tubing with a brushed finish.

Locks - Europrofile cylinder locks – keyed externally and thumbturn internally.

Door closer – TS83 Door Close rack and pinion device mounted on the head of the door.

Anti Finger Traps - All doors to incorporate anti finger trap claw hinges supplied by door manufacturer, not retro fit.  Anti Finger Trap hinges are required throughout.

Powered Opening - One set of V500 Main Entrance Doors to be operated electronically using ED200 Power Swing Door Operator opening motors.

Furniture for the doors will be as supplied by the system supplier either polyester powder coated or stainless steel as required.  The sub contractor shall bring to the attention of the architect those items of furniture and or fittings, which are not from the system suppliers’ own range.

The meeting stiles of the doors shall be rebated.

The door is to be side hung on internal/external hinges.

Additional furniture will be as determined and scheduled by the architect.

The system shall incorporate a thermally broken threshold rail/water bar against which integral EPDM gasketry can provide a seal.

The door system shall include within the lower door rail adaption profiles for brush and EPDM seals.

The threshold rail/water bar shall be of extruded aluminium providing a contact surface for the brush steel.

The system shall include for an EPDM zip in gasket foil to link with structural dpms and shall be located and mechanically held into the thermal isolator from incorporation between the internal and external elements of the finished floor surfaces.

Unless otherwise specified or agreed by the architect, in writing, obtain materials that are suitable for the purpose intended from the manufacturers with at least 10 years experience of manufacture of successful materials.

The sub-contractor shall provide a guarantee that component parts of the system, together with any ancillary fittings, will be available for a minimum period of FIVE years from the date of practical completion.

# Fixing:

The system may be reinforced as necessary and be complete with all structural members to resist the dead/imposed wind loadings.  The system is to be capable of transferring all loads subjected upon it to the main structure via sufficient permanent and, where necessary, flexible fixings.

# Thermal Movement:

The aluminium framework and glazing assemblies shall be contracted and installed in the prepared locations and openings with sufficient tolerance and, where necessary, expansion joints incorporated within the couplings to provide for expansion and contraction as will be caused by the climatic conditions and temperature changes, winter to summer, day to night, without buckling, distortion of joints, damage to the sealants or other detrimental effects over the temperature range –15oC to +35oC.  The design shall accommodate, noiselessly, the thermal movement within the combination units without distortion.  Details shall be prepared based upon the dimensions at 20oC and take account of the ambient temperatures at the time of assembly and installation.

L20/480	DOORSET FOR SUB-STATION (TO EDF’S APPROVAL

-	Manufacturer: SUnray .

-	Product reference: Fully louvred doubel steel door with removable panel over .

-	Finish as delivered: Polyester powder coated .

-	Frame and architraves: To suit .

-	Finish as delivered: Polyester powder coated .

-	Ironmongery: to suit .

-	Perimeter seals: As recommended by manufacturer .

-	Fixing: As recommended by manufacturer .

L20/520	SLIDING DOORS DG20A & DG20B

- Manufacturer:

- Schüco International KG, Whitehall Avenue, Milton Keynes. MK10 0AL.

- Tel: (01908) 282111  Fax: (01908) 282124.  Web: www.schueco.co.uk

-	Product reference: ASS50 Sliding Doors.

-	Performance:   Air permeability to EN 12207		600pa

Weather tightness to EN 12208	600pa

Resistance to wind load EN 12210	2000pa

-	Arrangement: Bottom Rolling on Stainless Steel Track.

-	Track system: Triple, Double and Single Track available.

-	Door leaf: Doors to be mechanically jointed using multi-chamber cleats.

-	Finish as delivered: Powder Coating as Section Z31.

-	Operation: Manual or Powered with Schüco E-Drive.

-	Ironmongery: Sliding Doors shall incorporate handles with gearboxes concealed within the vent frame. Door handles to be coloured to suit.

-	Other requirements: Glazing to incorporate DGU build up of 8mm /16mm cavity / 6mm.

L20/520/A	INTERNAL TIMBER FLUSH SLIDING DOOR DG06 & DG19

-	Manufacturer: Contractors choice.

-	Arrangement: Top hung: single leaf.

-	Track system: Hafele. Tel 51 8888, see below.  Removable mdf fascias.

-	Door leaf: approx 1700 (w) x 2200 (h) x 44mm thick , to be confirmed.

-	Finish as delivered: Prepared and primed.

-	Operation: Manual operated.

Ironmongery: HAWA-Junior 120B top hung door gear system, including Junior 120 top tracks ref 941.20.300 (length to suit), Junior 120B fitting sets ref 941.20.002 (trolley hangers, locking wrench, profile plugs, track stoppers, rubber buffers, assembly wedges). Aluminium lower tracks, surface mounted on existing floor, ref 943.37.830 (lengths to suit), with 2No. lower runners ref 943.36.035 to each door. 2No. d handles to each door.

L20/540	ACOUSTIC SLIDING/FOLDING PARTITION AREAS F01/F02

Manufacturer: Alco-Beldan or equal approved

- Product reference Visioplan 65N Sliding/Folding Partition, comprising 5 panels.  Top hung without floor guide. Sound reduction Rw53dB.  Melamine veneer. SAA edge profiles.  SAA anoldised aluminium ring handles and door latch.

EXECUTION

L20/710	PROTECTION OF COMPONENTS

-	General: Do not deliver to site components that cannot be installed immediately or placed in clean, dry, floored and covered storage.

-	Stored components: Stacked on level bearers, separated with spacers to prevent damage by and to projecting ironmongery, beads, etc.

L20/730	PRIMING/ SEALING

-	Wood surfaces inaccessible after installation: Primed or sealed as specified before fixing components.

L20/760	BUILDING IN

-	General: Not permitted unless indicated on drawings.

L20/770	DAMP PROOF COURSES ASSOCIATED WITH BUILT IN WOOD FRAMES

-	Method of fixing: To backs of frames using galvanized clout nails.

L20/790	FIXING OF WOOD FRAMES

-	Spacing of fixings (frames not predrilled): Maximum 150 mm from ends of each jamb and at 600 mm maximum centres.

L20/809	FIRE RESISTING/ SMOKE CONTROL DOORS/ DOORSETS

-	Installation: By a firm currently registered under a third party accredited fire door installer scheme in accordance with instructions supplied with the product conformity certificate, test report or engineering assessment.

L20/810	FIRE RESISTING/ SMOKE CONTROL DOORS/ DOORSETS

-	Gaps between frames and supporting construction: Filled as necessary in accordance with requirements for certification and/ or door/ doorset manufacturer's instructions.

L20/820	SEALANT JOINTS

-	Sealant:

-	Manufacturer: Contractors choice.

-	Colour: TBA.

-	Application: As section Z22 to prepared joints. Triangular fillets finished to a flat or slightly convex profile.

L20/830	FIXING IRONMONGERY GENERALLY

-	Fasteners: Supplied by ironmongery manufacturer.

-	Finish/ Corrosion resistance: To match ironmongery.

-	Holes for components: No larger than required for satisfactory fit/ operation.

-	Adjacent surfaces: Undamaged.

-	Moving parts: Adjusted, lubricated and functioning correctly at completion.

L20/840	FIXING IRONMONGERY TO FIRE RESISTING DOOR ASSEMBLIES

-	General: All items fixed in accordance with door leaf manufacturer's recommendations ensuring that integrity of the assembly, as established by testing, is not compromised.

-	Holes for through fixings and components: Accurately cut.

-	Clearances: Not more than 8 mm unless protected by intumescent paste or similar.

-	Lock/ Latch cases for fire 60 doors requiring > 60 minutes integrity performance: Coated with intumescent paint or paste before installation.

L20/850	LOCATION OF HINGES

-	Primary hinges: Where not specified otherwise, positioned with centre lines 250 mm from top and bottom of door leaf.

-	Third hinge: Where specified, positioned ______ .

-	Hinges for fire resisting doors: Positioned in accordance with door leaf manufacturer's recommendations.