## Meeting Log
Hazard Identification Meeting Details
Scheme Number and Title: | 20696 | Littlebrook 400kV Substation Replacement
Reference Material:
Document Number/Title | Version - Source (if not NG) | Dated | Used at…
NDP Stage: |  | 4.3
Meeting Date: |  | 2017-05-17
Attendees | Role and Organisation | Meeting Attendance (Attended / Absent / Not Invited)
Dan Bullock | Development Engineer
CDM-A
Lead Design Engineer (Assurance)
Design Engineer (Plant Assurance)
Investment Delivery Engineer
System Design Engineer
ETAM Ops
Project Engineer
Development Officer
Ramesh Akkenapragada | Design Engineer (P&C)
Iwan Watkin | Design Engineer (Plant) | Invited + Absent
Matthew Alexander | Design Engineer (Civil)
Colin Midmore | Design Engineer (Civil Assurance)
Freddie van der Linde | Principle Designer
David Kerven | Design Engineer (P&C Assurance)
Emanuele Salomone | Design Engineer (Cables)
|  | Invited + Attended | 4.2.
|  | invited + Dialed In | 4.3.
Invited + Absent
Not Invited

## Options
Options Description
|  | 4.2. Hazard Review Meeting |  |  | 4.3. Hazard Review Meeting
|  | Select Options to be considered in 4.2. Hazard Review (fill in at start of 4.2. Hazard Review) |  | Score (fill in after 4.2. Hazard Review) (A to E - see guidance tab) | Select Option to be considered in 4.3. Hazard Review (fill in at start of 4.3. Hazard Review)
Option Number | Description | Status | If not selected, why? |  | Status | If not selected, why?
1 | [8 empty] | 0 |  | 0 | 0 | 0
2 | [8 empty] | 0 |  | 0 | 0 | 0
3 | [8 empty] | 0 |  | 0 | 0 | 0
4 | [8 empty] | 0 |  | 0 | 0 | 0
5 | [8 empty] | 0 |  | 0 | 0 | 0
6 | [8 empty] | 0 |  | 0 | 0 | 0
7 | [8 empty] | 0 |  | 0 | 0 | 0
8 | [8 empty] | 0 |  | 0 | 0 | 0
9 | [8 empty] | 0 |  | 0 | 0 | 0
10 | [8 empty] | 0 |  | 0 | 0 | 0
[9 empty] | 0 |  | 0 | 0 | 0
1st option box
[7 empty] | If 1st option box is a | 1 | 0 | 0
[7 empty] | If 1st option box is a | 2 | 0 | 0
[7 empty] | If 1st option box is a | 3 | 0 | 0
[7 empty] | If 1st option box is a | 4 | 0 | 0
[7 empty] | If 1st option box is a | 5 | 0 | 0
[7 empty] | If 1st option box is a | 6 | 0 | 0
[7 empty] | If 1st option box is a | 7 | 0 | 0
[7 empty] | If 1st option box is a | 8 | 0 | 0
[7 empty] | If 1st option box is a | 9 | 0 | 0
[7 empty] | If 1st option box is a | 10 | 0 | 0
[8 empty] | If O5=1 | 0
If O5=0
0
|  | Considered |  |  | Considered
|  | Not Considered |  |  | Not Considered

## RegisterAt4.2
Hazard Register | Littlebrook 400kV Substation Replacement |  | Stage(s) Affected ("x") |  |  | Dealing With The Hazard |  |  |  | Communicating the Residual Risk |  | Add to Construction Phase Plan ("x") | Add to Health and Safety File ("x") |  | Development Aid ("x")
|  |  | Construction | Operation and Maintenance | Demolition/ Decommission | [9 empty] | Add to PEP Site/Works Info | Add to Risk Register | Investigate Via Survey
Hazard Applies to Option Number ("x")…
Item No. | Location / Task / Component / Operation / Condition | Hazard Description |  |  |  | Hazard Removal Method or Risk Mitigations | Mitigation Required By Date | Mitigation Owner | Mitigation Completed Date | Residual Risk Description | Reference to Document containing residual risk information

## RegisterAt4.3
Hazard Register | Littlebrook 400kV Substation Replacement |  | Stage(s) Affected ("x") |  |  | Dealing With The Hazard |  |  |  | Communicating the Residual Risk |  | Add to Construction Phase Plan ("x") | Add to Health and Safety File ("x") |  |  |  | Development Aid ("x") |  |  | 0
| NO OPTION HAS BEEN SELECTED YET |  | Construction | Operation and Maintenance | Demolition/ Decommission | [11 empty] | Add to PEP Site/Works Info | Add to Risk Register | Investigate Via Survey | 0
Do not delete
[14 empty] | Hazard Applies to Option Number ("x")… | [5 empty] | Password is Electric1
Item No. | Location / Task / Component / Operation / Condition | Hazard Description |  |  |  | Hazard Removal Method or Risk Mitigations | Mitigation Required By Date | Mitigation Owner | Mitigation Completed Date | Residual Risk Description | Reference to Document containing residual risk information
1 | Maintenance / repair / removal of existing buried services | New 132kV cables are to be laid between the 400kV and 132kV substations. Outside of the substations the route is yet to be determined but it will cross existing cables and services. There is therefore a risk to both the new and existing cables when future maintenance, repairs or removals take place. | x | x | x | Undertake a review of the cable layout to avoid cable crossings. Consider excavations on future projects or maintenance works and the impact it may have. Consider how maintainable trough design is. A route has been chosen that minimises clashes with existing cables. This includes a HDD under the 33kV cables associated with the adjoing UKPN 33kV substation that will require exceptional care during installation. The residual risks are those associated with the installation and maintenance of cables in congested areas. The Contractor will therefore have to comply with the usual requirements for excavations in these environments. | 2017-07-30 | FEED Contractor | 2017-07-30 |  |  | x |  |  |  |  | x | x | x
2 | RMHZ | Risks associated with any RMHZ | x | x | x | None identified. PC to verify with Employer during bidding and prior to construction. | Construction complete | PC and Employer | Open |  |  | x |  |  |  |  | x | x
3 | Commuting and travel in area between 400kV and 132kV substations | New 132kV cables are to be laid between the 400kV and 132kV substations. Outside of the substations the route is yet to be determined. The land between the substations has public access so there is a risk to members of the public and road users during the cable excavation work. | x | x | x | Investigate the route that presents the lowest risk during excavation and installation. The chosen route is a compromise between that limiting contact with third parties during construction and the risk of damaging existing services. The remaining risks arre those associated with the installation of cables in areas accessible to third parties such as roads and verges. All work shall be carried out in accordance with the recommended procedures and best practice and in consultation with the Local Authority. | 2017-07-30 | FEED Contractor | 2017-07-30 |  |  | x |  |  |  |  | x | x
4 | Excavation works (especially within SGT3 site) | Impact with buried services and/ or unknown ground contamination | x |  |  | Consult with ETAM Ops to retrieve pre construction information for both sites. This to include: Underground Hazard Plans Information for SGT3 site from UKPN Existing survey reports Once information is ascertained, various surveys can be planned for. | 2015-09-01 | National Grid
8 | Excavation works within the sites | Exposure to asbestos | x |  |  | The potential to be exposed to asbestos from these works is from transformer demolition/ replacement and excavation works. The replacement of the transformer itself should be suitably managed by the legal requirement to undertake an asbestos refurnishment survey. Prior to undertaking both works the pre construction information needs to be obtained. Consult with ETAM Ops to retrieve the Asbestos Management Plan. for both sites. | 2015-09-01 | National Grid
4 | Operation of electrical equipment | Due to the flood risk of the site, persons may operate electrical equipment while in contact with water. | x |  |  | Determine the flood risk levels and evolve a suitable design. Requirements to be added to the WI. Also include a requirement to provide suitable access where equipment is raised. Specific equipment that may require protection from flooding such as MKs, control boxes and mechs, etc to be listed in WI. The flood risk assessment shows that there is one area in the north-eastern part of the substation that may be exposed to flooding. However this will be built up to the level of the rest of the substation and no exceptional risks remain oncethe site is constructed. However the risk will exist during the Construction of the substation. The PC shall develop appropriate RAMS for specific activities including a strategy to manage risk of flodding for the entire site. The flood resilience level has been calculated using National Grid policy guidance TS 2.10.13 Issue 2 (2016) “Flood Defences for Electricity Substations, Generic Electricity Substation Design Manual for Civil, Structural and Building Engineering” which sets up minimum design criteria for new site drainage systems for the 30, 100 and 1000 year rainfall events over the lifetime of the development. No exceptional risk remains although it should be noted that the site is (in accordance with National Grid policy) not protected angainst overtopping of the flood defences in the area. The substation will be partly built in an existing depression and we shall make the level up so the site is all situated at 2.6mAoD. All runoff from the catchment is dealt with on site however, the displacement MAY increase flood levels in the area to the north of the site for given design storms. It will be for the new landowner of the surrounding areas to deal with all runoff on their site without infringing on National Grid land. | 2017-07-30 | FEED Contractor | 2017-07-30 |  |  | x |  |  |  |  | x | x
10 | Undertaking construction works associated with the project | Impact/ clash with adjacent Principal Contractor's | x |  |  | Collate information regarding planned capital delivery projects and scheduled ETAM Ops maintenance works to determine any potential clashes with the projects. A review can then be undertaken to determine where any clashes can be avoided through consideration of work sequencing and construction methodologies on the site. Outage consideration will be consdered through TP153 meetings. Identify cases where there is clearly a known conflict or concurrence. Rest to be fleshed out through TP153 process. DE/PE to confirm other works at the site in the same timescales. | 2015-09-01 | National Grid
5 | Installation/excavation/construction/maintenance of new West Thurrock cable/GIB and AIS kit under oversail | Restricted access to equipment situated under existing Kemsley/Rowdown 2 circuit until it is moved. | x | x | x | Can the sequence be changed to reduce the hazard during construction? Are proximity outages available? Can the equipment be laid out in a way that reduces the risks? The construction and outage sequence has been changed to eliminate hazard. | 2017-07-30 | FEED Contractor | 2017-09-25
6 | Working at height on elevated platform GIS substation during construction / installation / maintenance / decommissioning | The flood risk may neccessitate the sub being constructed on an elevated platform, elevating the switchgear above the flood risk levels. This creates working at height hazards. | x | x | x | Elevation of platform to be kept to a minimum. All construction, maintenance and demolition activities to be connsidered and fall protection integrated where this is the best solution. OPS to be consulted regarding operational aspects of the design. FRA indicates that an elevated platform is not required. | 2017-07-30 | FEED Contractor | 2017-09-25
7 | Movement / operation of large cranes for GIS and SGT removal, installation of the new CSE and demolition of the existing 275kV ohl gantries | Insufficient ground bearing capacities | x |  |  | Consult with ETAM Ops to retrieve existing information if up to date and available or undertake surveys to ascertain the ground bearing capacity for the locations of where the crane will be situated when undertaking lifting operations. Ground Investigations have been undertaken and indicate that the soil may have sufficient load bearing capability but this should be verified for each appliance used on site. | 4.3 Completion | Jacobs | 2017-10-13 |  | Littlebrook 400kV Sub-station Scheme, National Grid, Geo-environmental Interpretative Report on Ground Investigation, PDD - 20696 - REP - 102 ¦ 00, 01/07/2017, 20696 | x | x |  |  |  | x | x | x
8 | Existing GIS demolition | Inadequate clearance and / or insufficient space to allow a 24t crane access to existing GIS for demolition and removal of equipment to be re-used. | x |  | x | Some of the anciliary equipment and transformers will be moved wile the existing substation is live. Proximity outages may be required to allow removal of the latter. The rest of the substation will be de-energised before demolition of the existing GISbegins. | Construction start | Employer and PC | Open |  | Substation layout PDD-20696-LAY-009 and SRD | x |  |  |  |  | x | x
9 | Undertaking construction activities in the 400kV and 132kV compounds. | Impressed Voltages | x |  |  | Impressed voltage risks to be identified during the detailed design and construction phases and communicated to site personnel. To be managed in accordance with TP141, TP243 and CSSOW. | Construction start | National Grid and PC | Open |  |  | x
16 | Delivery of SGT to site (off site consideration) | Insufficient ground bearing capabilities | x |  |  | Consider 132kV cable / GIS disconnection for isolation and earthing | 2015-09-01 | National Grid
10 | Working in the existing substation | Exposure to high transfer voltages and step and touch potentials due to partial and/or inappropriate staged decommissioning of the existing earthing | x | x | x | PC to develop staged design of the earthing system. | Construction start | PC | Open |  |  | x |  |  |  |  | x | x
11 | Excavation in both compounds by NG PC and Contractors working on behalf others. | Service strikes by PC due to unknown service routes. There is a number of services to be diverted from the site by their owners. There will be repeated excavations in close proximity to live/pressurised services when the diversions are done. | x |  |  | Surveys were carried out of the new 400kV substation and the information has been provided on the Hazard Plan. Partial surveys were carried out along the new 132kV cable routes and in the the existing 132kV substation. PC to coordinate the work of the different asset owners. The design of the new routes should take into account future maintenance, repairs, construction and demolition on the site. | Construction start | Employer and PC | Open |  | 20696, LITTLEBROOK 400KV REPLACEMENT, HAZARD PLAN, LITTLEBROOK 400kV SUBSTATION, PDD-20696-LAY-002, Rev 00 | x |  |  |  |  | x | x
12 | Working in the new substation | Exposure to high transfer voltages from the existing substation prior to the new sub earthing being stablished and bonded to the existing one. |  |  |  | Duplicate entry
13 | Excavation of areas in the existing substation | Exposure to asbestos | x |  |  | Combined with Hazard 28.
14 | Access to GIS for maintenance and inspection. | Gas sampling points and pressure gauges to be accessible without the use of a MEWP so they shall be brought down to ground level or platforms provided. | x | x | x | The Employer needs to confirm what was supplied with the Tilbury GIS (being re-used here) and if necessary request additional measures. | Construction start | Employer | Open | This will actioned and agreed between National Grid and Principal Contractor during 4.4 |  | x | [5 empty] | x
15 | Demolition of existing stuctures, cables/ducts/troughs and panels | Exposure to asbestos | x | x | x | Ensure an asbestos refurbishment survey is undertaken by a competent asbestos contractor prior to undertaken any intrusive works associated with the SGT’s | Construction start | Employer and PC | Open |  | Asbestos Management Plan (Ref) Asbestos Surveys (Ref) | x |  | x | x | x |  | x
16 | Existing gantries | Suitability for re-use | x |  |  | Now captured for all equipment in Hazard 34
17 | Work in the cable tunnel | There is an asbestos shield in the cable tunnel. Demolition of part of the tunnel or core drilling into the tunnel may release asbestos dust. | x |  | x | The design to be altered so that the work required in the tunnel is reduced to the minimum. The cable jointing design purposely placed outside tunnel to reduce risk. Should not be altered without consideration. | Construction start | Employer and PC | Open | Asbestos exposure | Cable Route diagrams PDD-20696-CAB-001 | x | [5 empty] | x | x
18 | Operational switching | Nomenclature changes; drawings won't be updated and temp labelling applied. | x | x |  | Use of temporary lebelling and nomenclature agreed at 4.3. Details to be implemented in PEP and commissioning programme. | FEED Completion | FEED Contractor and Employer | 2017-09-25 |  |  | x |  |  |  |  | x
19 | Excavation | Some cable crossings may be very deep. Consider alternatives. | x | x | x | Deep crossing of existing services could not be avoided as this would have increased the risk of service strikes. | FEED Completion | FEED Contractor | 2017-09-25 |  |  | x | [5 empty] | x | x
20 | Working in cable tunnel and deep excavations | Exposure to SF6 due to the high leakage rate of the existing GIS. Low lying areas, troughs and ducts will be particularly at risk. SF6 sinking into low areas. | x |  | x | SF6 monitoring to be put in place. | Construction start | PC | Open |  |  | x
21 | Excavations and movement of heavy equipment on land. | Medium to high risk of unexploded ordinance on site. | x | x | x | Undertake magnemometer survey as soon as site is cleared. All drilling setc to be supervised and carrie dout in accordance with best practice. | Construction start | PC | Open |  | UXB Report EES0593 R-01-03 | x |  |  |  |  | x | x
22 | Work on earthing and bonding | Exposure to high potentials due to out-of-date earthing condition surveys and incorrrect recording of defects corrected. | x |  | x | PC to review the last earthing survey undertaken for the site by ERM and determine if any of the defects listed there will present a risk during the construction of the new site and the decommissioning of the existing site. | Construction start | PC | Open |  | ERM Report for Littlebrook ERM R194 | x | [6 empty] | x
23 | Construction of new compound and cables | Drowning due to exposure to deep water and flooding of excavation. | x |  | x | Combined with Hazard 4.
24 | Construction and maintenance of new equipment | Risk of injury and equipment damage due to poor coordination between Employer's contractors if the GIS is to not installed by the OEM. | x | x | x | Develop DoR Schedules as soon as National Grid's contracting strategy is known to ensure that the design is fully coordinated. Provisional DoRs have been developed and can be found in the WI. | Detailed Design Start | Employer | Open | This will actioned and agreed between National Grid and Principal Contractor during 4.4 |  | x |  |  |  |  | x | x
25 | Construction of the new substation | Injury or death and damage to equipment on site due to inadequate coordination caused by a large number of acivities simultaneously taking place on site. National Grid's contracting strategy should consider the number of skills and teams required on site at any one time, especially where these are not contractually under the control of the PC | x |  |  | Allow enough time in the programme to segregate the construction and commissioning of the GIS in distinct stages while other actvities on site are limited. | Contract Award | Employer | Open |  |  | x | [5 empty] | x
26 | Construction of the new substation | Exposure to high voltages to due proximity working. Cladding of the new building and erection of the roof will be undertaken while the Hurst and West Thurrock circuits passing by are still live and in relatively close proximity. There is also a risk of damage to the completed building when the existing overhead conductors are removed. | x |  |  | The new substation has been put in a position and orientated in a manner that maximises the clearances. All lifts to be agreed with the SAP. | 2017-07-30 | Feed Contractor | 2017-09-25 |  | Layout for new Substation PDD-20696-LAY-009 | x |  |  |  |  | x | x
27 | Excavations | Exposure to dangerous contaminants during excavations on the land for the new substation. | x | x | x | Combined with Hazard 28.
28 | Excavations | Exposure to dangerous contaminants (including asbestos) during excavations on the land for the new substation. | x | x | x | Soil contamination was determined as part of the GIs and there was no evdidence of signifcant contamination except for asbestos. The sampling data is only appropriate to the specific samples, and elevated soil concentrations may be identified elsewhere within the site. Consult with ETAM Ops to determine the extent of asbestos within the land surrounding the SGT’s from their existing records e.g. asbestos management plan (also see Hazard 27). | Construction Start | PC and Employer | Open | Asbestos contaimation of the soil measured as pasrt of the GIS and while 17 borehole samples contained asbestos below the quanitifcation limit, 2 were above it. Prior to any further works that will disturb the ground in this area, the contractor undertaking the works will require the undertaking an asbestos risk assessment in accordance with the Control of Asbestos Regulations 2012. Asbestos was found close to the surface and this should be kept in mind when stripping the top soil. | Littlebrook 400kV Sub-station Scheme, National Grid, Geo-environmental Interpretative Report on Ground Investigation, PDD - 20696 - REP - 102 ¦ 00, 01/07/2017, 20696 | x | x |  |  |  | x | x | x
29 | Remedial work on tower | Working at height. The double angle bars on tower ZBG013 were found to require additional stitch bolts along the members in order to strengthen them. These are located on the top crossarm and therefore will require additional tower climbing and drilling holes at height alongside the downlead stringing works. | x |  |  | None identified. | FEED Completion | FEED Contractor | 2017-10-13 |  |  | x |  |  |  |  | x | x
30 | New downlead installation | Exposure to high voltages to due proximity working. In the present configuration the proposed downleads for ZBG013 would infringe circuit to circuit clearances with the conductors in span YL026-YL027 which over sails them. | x |  |  | Sequence arranged so that the downleads on tower YL026 are installed first to remove span YL026-YL027 before the ZBG013 downleads are installed. | Construction Start | Employer | Open |  | SRD | x | [5 empty] | x
31 | Removing existing downleads and intalling new ones. | Injury or death and damage to third party propoerty from conductors falling on public road during new downlead installation On Hurst 1 and circuits. | x |  |  | It has been assumed that the road below the Hurst CCT1 and CCT2 gantries will be closed and not be operational prior to the downlead installation. Alternatively scaffolding will be required. | Construction start | Employer and PC | Open |  |  | x | [5 empty] | x
32 | Service strike | There is a large number of services to be diverted from the site and these do not belong to the same owners. There will be repeated excavations in close proximity to live/pressurised services when the diversions are done. | x |  |  | Combined with Hazard 11.
33 | Moving equipment and vehicles into and out of the laydown area and welfare compound. | Contact with live high-voltage conductors. Laydown partly located under live circuits. | x |  |  | The laydown and welfare areas have been redfined to move it from under the oversail. Th latter is now only proposed for small vehicle parking. | 4.3 complete | FEED Contractor | 2017-10-13 |  | CDM Plan PDD-20696-LAY-003 | x | [5 empty] | x
34 | Equipment operation | Injury or death and damage to equipment due to inappropriate, old or damaged equipment being re-used. All the equipment to be re-used have not been assessed for suitability. | x | x |  | Carry out asset condition surveys. | Contract award | Employer and PC | Open |  |  | x | x |  |  |  |  | x
35 | Operation of third party assets in the vicinity of the new substation. | The EPR for the site is high and the associated 650V and 1700V potential contours extend approximately 1200m and 600m respectively. This will have an impact on a number of third parties with potential damage to third party equipment including telecoms, rail and gas/petrochemical installations and explosions. |  | x | x | Carry out surveys of affected third parties and implement mitigation. | Energisation | Employer | Open |  | ERM Report for Littlebrook ERM R194 | x |  |  |  |  | x | x | x
36 | Construction of new substation | Exposure to airbourne contaminants due to demolition of adjoining powerstation. May include asbestos. | x | x | x | PC to install asbestos monitoring. Employer to coordinate with the power station owner and communicate risks to PC. May be delays if there are significant quanitiies of contmination in the power station. | Construction Start | Emplyer / PC | Open |  |  | x | [5 empty] | x
37 | Diverting services between the existing sub and 132kV sub and cable tunnel headhouse | Exposure to high transferred potentials. | x | x | x | New equipment to be connected to the earthing system in accordance with the requirements of the NSIs. PCC to incorporate procedure into Impressed Voltage Managment Plan. | Construction start | PC | Open |  |  | x | [5 empty] | x
40 | Local residents' activities | Disruption and discomfort due to obtrusive light | x | x |  | Lightning plan during construction and for final arrrangement to take into account the surrounding third parties. | Construction start | PC | Open | Disruption and discomfort due to obtrusive light |  | x |  |  |  |  | x
41 | Construction and operation of the new substation. | Equipment security and fly-tipping | x | x | x | The proposed fence has been extended to improve the security of the new 400kV substation. The PC shall consider additional arrangements during construction. | Construction start | PC | Open | Equipment security and fly-tipping |  | x |  |  |  |  | x
42 | Construction and operation | Due to all the other construction activities in the area there may be a heightened security risk, including at the GIS laydown area in the 132kV subbstation compound. | x |  |  | Additional security measures to be put in place. | Construction Start | PC | Open |  |  | x
Selected Option:

## Discussion Aid
Primary Guide: Hazards Associated with… | Secondary Guide: Example Hazards Prompts
General Design Considerations | Residual hazards from the H&S File
Human error
Durability
Extendability
Prefabrication
Site establishment, Lay down areas,
Add as necessary…
The System and "Safety from the System" During Construction and Throughout Asset Life | Residual hazards from system design
Operating Modes / Compatibility Issues
Impact on Remote Ends
Outages Sequences / Proximity Outages
Electrical Clearances / Physical Clearances
Induced Voltage / Induced Current
Testing / Commissioning / Handover
Rise of Earth Potential
Add as necessary…
The Site and Work Environment During Construction and Throughout Asset Life | Contaminated Ground
Unstable Ground / Uneven Ground
Drainage / Waste / Effluent
Chemical Issues / Biological Diseases
Ecology / Biodiversity / Invasive Species
Noise / Disturbance
Climatic Conditions / Weather / Flood / Lightning
3rd Paries / Cultural / Social / Human Factors
Adjacent Land Use
River / Stream Management
Harmful substances
Working space
Add as necessary…
Existing Nearby Activities and Equipment or Proposed New Activities and Equipment During Construction and Throughout Asset Life | Hazard Zones
Emissions
Missile Generation / Impact Damage
Dust - occupational health
Vibration / HAVS / Heat
Asbestos
Existing Underground Services / Temporary Services
Spacial Constraints
Existing Structures
Pedestrian Movement
Vehicle Movement
Public / 3rd Parties
Security Issues
Equipment Failure
Maintenance
Personnel and Equipment Access / Egress
Touch Potential
Manual handling
Add as necessary…
Site Construction Activities During Construction and Throughout Asset Life | Work at Height
Work Over / Near / In Water
Confined Spaces
Lifting Operations
Temporary Works
Hot Works
Install / Demolish Sequence
Road / Rail / River / Other Crossings
Excavations and Earthworks
Scaffolding
Add as necessary…
End of Asset Life and Demolition | Tensioned Structures
Pressurised Equipment / GIS
Hazardous Waste / Asbestos
Transformer Oil
Contaminated Ground
Earthworks and retaining structures
Residual hazards after demolition
Disposal/recycle, etc
Add as necessary…
Note on B2: Review the contents of the H&S file for example the existing site hazard plan
Note on B3: Have new equipment/designs taken into account human error? Have all systemic conflict scenarios been evaluated and human error probability considered in the design? Is their any possible mal operation of equipment as configured either in error or misuse?
Note on B4: What adverse conditions may arise and how have they been mitigated against? Protective features assuring resistance to mechanical impacts, and corrosive environments?
Note on B5: Is the proposed new equipment extendable in the future? Will any future extension of the proposed equipment introduce new hazards?
Note on B6: Can any hazards be mitigated by prefabrating equipment off site and transporting in pre-assembled parts?
Note on B7: Does the proposed site set up minimise hazards, are laydown areas, parking, offices, etc suitably positioned to minimuse hazards?
Note on B9: Does the proposed modication to the network introduce any hazards? Do the system options differ in their hazards?
Note on B10: Will the proposed new equipment operate safely in conjuciton with the existing equipment? Are there any knock on effects from the operation of the new equipment?
Note on B11: Are other sites affected by the proposed new equipment or the construction work?
Note on B12: Does the proposed sequence of outages minimise the hazards? Is there potential to cause harm due to the outages arranged? Are the outages long enough? Are works in the proximity of live equipment?
Note on B13: Does the construction work take place outside of suitable electical clearance distances? Are there any physical clearances that need to be maintained during the works or during the future operation of the proposed new equipment?
Note on B20: Run off, flooding, locating exisiting services, new services, high voltage proximity
Note on B23: Environmental/nuisance and occupational health
Note on B25: National Grid: Travellers, trial bikers, crime, grantors, aggressive neighbours, security
Note on B28: National Grid: Lead, Chemicals, PCB's, Flammables, Radiation, Fumes - occupational health, Hydrocarbons
Note on B31: National Grid: Risk Management Hazard Zones / Fire / Explosion / Missile Generation / Impact Damage, Equipment Failure
Note on B40: Site vehicle segregation, Personnel and Equipment Access / Egress
Note on B41: Vehicular Access Routes / Transport, Large load transportation, Crane access, Number, scale, size & impact of vehicles
Note on B50: Scope for off site or on ground assembly?
Note on B58: Site clearance and topsoil/earthworks management

## Guidance
Guidance For Using The Hazard Register
Purpose: | The purpose of this hazard register is to contribute to a reduction in hazards and risks during construction, commissioning, operation, maintenance and demolition of any addition/alteration to NG systems/networks and to compare options in 4.2. from a "safety by design" perspective and contribute to the Whole Life Value analysis or the Optioneering Report. The register may also help to track the performance of the Principal Contractor in their identification and mitigation of hazards during the 4.4. stage. Specific responsibilites of CDM duty holders are addressed as follows:
Client Duties: | The hazard register assists National Grid to meet its legal obligation as the Client under the CDM Regulations to:
~ Provide pre construction information to designers and contractors.
~ Providing information relating to Health and Safety File.
Designer Duties: | The hazard register assists National Grid to meet its as the Designer under the CDM Regulations to:
~ Contribute to eliminating hazards and risks during design and to provide information about remaining risks.
~ Provide information relating to Health and Safety File.
CDMC Duties: | The hazard register assists the CDMC in their legal obligation under the CDM Regulations to:
~ Coordinate health and safety aspects of design work.
~ Facilitate good communication between Clients/Designers/Contractors
~ Identify, collect and pass on Pre Construction Information.
~ Preparing and updating the Health and Safety File.
General: | When the spreadsheet is first opened macros/content should be enabled. Initially save the spreadsheet in a folder of your choosing so that future autosaves occur without any problems.
No separate Hazard Review Minutes are required to be produced, the hazard register itself logs the meeting details.
This register is not intended to be a standalone optioneering document. It is not a quantitative assessment of options. The Options tab provides a high level qualitative comparison.
In order to work through the spreadsheet quickly in a meeting, nominate a "typer" who is fast with excel.
Coloured boxes should not be filled in, if a box is not applicable type n/a.
Think about the hazards that are already present on site which may affect the proposed solution (hazards that may impact on its design, construction, operation, maintenance and/or demolition).
Think about the hazards that the proposed solutions may introduce to the site and surrounding area. Does the proposed option/solution introduce enduring hazards after the solution is in place? Are there any hazards present during the construction, operation, maintenance and demolition of the proposed solution?
Consider issues that are specific to the scheme/options. Generic hazards such as general trip hazards etc are assumed to be covered by general site competency. Only items prompting a specific mitigation or non standard construction methods should be included in the register.
A Hazard Register is to be completed in both 4.2. and 4.3. stages, unless it is deemed only required at 4.3. due to either the outcome of a direction setting meeting or maybe because the scheme is transitioning from TP146.
The Discussion Aid tab offers ideas of the sorts of discussions to take place in hazard reviews.
Meeting Log tab | Enter the scheme number and title
State the reference documents and revision numbers of these documents. It is important to base the meeting discussion on well defined scope boundaries. More rows can be inserted here if necessary. Example documents are Layouts, Project Briefs, Existing Site Hazard Plans, PEP's etc.
State the NDP stage and the meeting date. State the attendees and add to this list of attendees for subsequent meetings if required.
Consult TP188 main document for guidance on who should attend the hazard meetings.
4.2. Hazard Review Meeting
Options tab description and status at 4.2. | Describe the options in enough detail to clearly distinguish between them. The full option description resides in the Project Brief.
Before completing the Register At 4.2 tab select which options are to be considered in the 4.2 hazard review. A judgement is required as to which options are worth considering. If several options will have the same set of hazards, there is no need to repeat options. State the reason for not considering an option in the 4.2 hazard review.
Register at 4.2 tab | Direction Setting Meeting 1 should determine the requirements at 4.2. For example a Fittings Only OHL scheme may only have two options (replace fittings or do nothing). In this case there is no need to use the hazard register to aid optioneering, and the register can be completed for one option only.
At the 4.2 stage just consider the hazards that are applicable to each option being considered (try to keep the number of feasible options below 4).
When first creating a hazard register for a scheme, it is suggested that site visit is udnetaken as part of the hazard review meeting. This will allow the scheme team "brainstorm" the hazards during a site walk around. Following this, a structured approach using the guidewords can be used to make sure nothing is missed.
For each hazard identified, fill in all the free text columns or mark with in "x" if indicated in the column heading.
Only include hazards where the mitigation causes non-standard design/construction techniques, or that may generate future maintenance/demolition issues in the future.
Type an "X" in each column/option for which the hazard applies.
The "Dealing With The Hazard" columns may help to eliminate, reduce, isolate or control a hazard/risk. However in some cases the hazard must be left for the Contractor to mitigate. A mitigation may be to impose a design constraint, in which case by completing the works information accordingly the mitigation completion date can be the same date as the date of issue of works information to the Contractor.
Where a hazard or residual risk remains, this can be described and handled in the "Communicating the Residual Risk" columns.
In dealing with the hazard, the scheme team may introduce design constraints. If this is the case put an "x" in the Development Aid column titled "Add to PEP Site/Works Info", in order to aid the Development Engineer in completing 4.3. documentation at a later stage.
Where an identified hazard also poses a risk to the scheme commercially, putting an "x" in the Development Aid column titled "Risk Register", is a useful reminder for inclusion in future Risk Reviews.
Where further consideration is required via a survey, the Development Aid column titled "Investigate Via Survey" should be stated "x".
Options tab scoring | After completing the Register At 4.2 tab give each considered option an overall hazard score A to E (see table below). If the most serious hazards were to manifest into events, consider the events' severity and likelihood and apply an overall score to each option. It is one score per option, not per hazard.
4.3. Stage
Options tab 4.3 status | Before completing the 4.3 Register tab select which options are rejected and which is selected. Only the selected option should be assessed in more detail at 4.3.
Register at 4.3 tab | This tab is to be used by the Client (National Grid) only. It should not be the main method of hazard identification to be utilised by the Contractor.
In the 4.3. Register you can import the data from the 4.2. tab (for the selected option only) by single clicking the "Import Data from 4.2. Register" button.
By importing the data from the 4.2 register, any existing data in the 4.3 register is overwritten and lost. The spreadsheet will autosave when the "Import Data from 4.2. Register" button was clicked, therefore to undo the import, exit Excel and reopen the file.
Add more detail to the hazards during the 4.3. Hazard Review, using further detail gained during development via surveys etc.
Work through the guidewords in the meeting and discuss if hazards exist. If so, include the description, state the cause and the mitigation.
Only include hazards where the mitigation causes non-standard design/construction techniques, or that may generate future maintenance/demolition issues in the future.
The "Dealing With The Hazard" columns may help to eliminate, reduce, isolate or control a hazard/risk. However in some cases the hazard must be left for the Contractor to mitigate.
Where a hazard or residual risk remains, this can be described and handled in the "Communicating the Residual Risk" columns.
The "Mitigation During Development" may be a scheme team decision on scope or may introduce design constraints. If this is the case put an "x" in the Development Aid column titled "Design Constraints".
Where an identified hazard also poses a risk to the scheme commercially, putting an "x" in the Development Aid column titled "Risk Register", is a useful reminder for inclusion in future Risk Reviews.
Where further consideration is required via a survey, the Development Aid column titled "Investigate Via Survey" should be stated "x".
At the 4.3 stage this register is meant to test the proposed solution to check appropriate decisions have been made to remove hazards completely or reduce their risk.
Export Data | By clicking the Export Data button, a separate excel sheet is created with a list of the hazards shown in the RegisterAt4.3. tab. This sheet should be saved with a unique filename including the scheme number and site. This file is the externally facing hazard register. It is to be embedded in the PEP as works information. Upon contract award this file is to be used to track hazards through the delivery phase of the project is to be completed by the Principal Contractor. In addition to this the the Principal Contractor is expected use their own "industry standard" methods for hazard management.
4.4. Stage
Hazard Register File | The excel file that is embedded in the PEP forms part of Works Information. This is the externally facing hazard register. It does not provide details of the rejected options, only the selected option.
The externally facing hazard register is to be updated by the Contractor during 4.4., in addition to the overall the management of hazards during detailed design and construciton stages.
The Contractor shall demonstrate that they are managing the hazards by updating the externally facing hazard register, and the Client may request to see the Contractor's other hazard management techniques/methods. The Contractor should not rely on the externally facing hazard register as their only means of hazard management. It has been designed for use with the level of detail known at 4.2. and 4.3. stages only.

## ForPEP (hidden)
Hazard Register | Littlebrook 400kV Substation Replacement |  | Stage(s) Affected ("x") |  |  | Dealing With The Hazard |  |  |  | Communicating the Residual Risk |  | Add to Construction Phase Plan ("x") | Add to Health and Safety File ("x")
| 2026-07-29 |  | Construction | Operation and Maintenance | Demolition/ Decommission
Date Created: | 2015-12-03
Item Ref. No. | Location / Task / Component / Operation / Condition | Hazard Description |  |  |  | Hazard Removal Method or Risk Mitigations | Mitigation Required By Date | Mitigation Owner | Mitigation Completed Date | Residual Risk Description | Reference to Document Requiring Update
1 | Maintenance/ removal of existing buried services | Impact with other buried services due to cable crossing | x | x | x | Undertake a review of the cable layout to avoid cable crossing. Consider excavations on future projects or maintenance works and the impact it may have. Consider how maintainable trough design is. Location of new marshalling kiosks relative to troughs and transfromer MKs chosen to mimimize aboveground cables (eg. in bund) and utilise existing troughs ratherr than creating new crossings. | 2015-09-01 | Jacobs | 2015-09-17
2 | Undertaking works adjacent to SGT5A (predominantly 400kV compound fence) | Works within live risk management hazard zones associated with the OESB03/13 that also prevented the FEED contractor from access for survey works in the affected areas. | x |  |  | Consult with ETAM Ops to retrieve further information regarding the risk management zones, areas covered by the risk management zones, and potential solutions for removal of the risk management zones prior to commencing works for SGT5A. | 2015-09-01 | National Grid
3 | SGT5b | Exposure to fire causing damage to equipment in adjacent bays and the relay room. SGT5a will have a FBW towards SGT5b that will only partially limit the FDZ overlap on SGT5b. |  | x |  | The relay room shall be hardened by the Contractor. Based on information obtained by the DE on resilience of the netowrk (confirming that a long term outage of both SGTs is not acceptable), the SGT5a FBW has been extended as far as possible. However, some FDZ overlap on SGT5b remains and a derogation from the requirements of TS 3.1.3 has been raised. | 2015-09-01 | Jacobs / National Grid | 2015-10-31 | FDZ overlap on SGT5b remains and a derogation from the requirements of TS 3.1.3 has been raised. | Derogation from the TS (WW_Deviation_FDZ_23_10_15), PEP and SGT5a layout PDD-6253-LAY-001 | x | x
5 | Removal of bunds / Transformer replacement | Exposure to contamination around the bund | x |  |  | Based on a visual inspection of the bund and its immediate surroundings, it is expected that there will be oil contamination in the bund and potentially in the soil below and around the bund. Further surveys are to be undertaken to ascertain the full extent of the contamination to plan for. | 2016-01-31 | Jacobs | 2015-10-31 | Exposure to contamination around the bund | The GI is programmed to be undertaken w/c 11th Jan. Residual risks to be identified when factual and interpretive reports become available. | x
6 | Accessing/ maintaining valve points on the SGT's | The noise enclosure design does not take into account high-level inspection and maintenance that may be required, creating confined and inaccessible spaces | x | x |  | SGT noise enclosure specification to include an explicit requirement for these considerations. | 2015-09-01 | PC | Detailed Design | Noise enclosure design does not take into account high-level inspection and maintenance that may be required, creating confined and inaccessible spaces | SGT5a and SGT3 GAs from bulk purchase supplier | x
7 | Design of the access stairs for SGT5A | The standard stair design creates confined spaces and limited areas for movement if the existing bund is not modified. | x | x |  | The stair design to modified to fit within the existing bund without creating confined spaces or areas where access could cause injury (overhangs or narrow spaces) | 2015-09-01 | Jacobs | 2015-10-13 | The standard stair design creates confined spaces and limited areas for movement if the existing bund is not modified. | SGT5a layout PDD-6253-LAY-001 and elevation PDD-6253-ELE-001 | x
9 | Operation of electrical equipment (SGT3 and SGT5A) | Electrical equipment in contact with water/ impact with persons maintaining equipment |  | x |  | Requirements now determined and added to the PEP. PEP also includes a requirement to provide suitable access where equipment is raised. Specific equipment such as MKs, control bioxes and mechs, etc to be listed in PEP. The following flood levels were applied: The flood resilience levels are: for 400kV site 15.65m AOD – 1:1000yr. for 275kV site it is 15.76m AOD – 1:1000yr. | 2/101/5 | Jacobs / PC | 31/10//2015 | Electrical equipment in contact with water / impact with persons maintaining equipment | PEP Section E22 for SGT3 and SGT5A | x | x
11 | Access / maintenance to aeriels under the conductor during installation of SGT5A | Insufficient access to aeriels situated under conductor during and after installation of SGT5A | x | x | x | Undertake review to consider the access arrangements to the aeriels for ETAM Ops during and after completion of works. Discussions to be undertaken to determine the necessity to increase the overall scope of the project to address the issue. DE to seek clarification from ETAM OPS. | 2015-09-01 | National Grid | Construction | Insufficient access to aeriels situated under consductor during and after installation of SGT5A | None available | x | x
12 | Movement/ operation of large cranes for SGT installations (SGT3 and SGT5A) | Insufficient ground bearing capacities | x |  |  | Consult with ETAM Ops to retrieve existing information if up to date and available or undertake surveys to ascertain the ground bearing capacity for the locations of where the crane will be situated when undertaking lifting operations. | 2016-01-31 | Jacobs | 2015-10-31 | Insufficient ground bearing capacities | The GI is programmed to be undertaken w/c 11th Jan. Residual risks to be identified when factual and interpretive reports become available. | x
15 | Undertaking construction activities in the 400kV and 275/132kV compounds. | Impressed Voltages | x |  |  | Impressed voltage risks to be identified during the detailed design and construction phases and communicated to site personnel. To be managed in accordance with TP141, TP243 and CSSOW. | 2015-10-02 | National Grid and PC | Detailed Design | Impressed voltage risks to be identified during the detailed design and construction phases and communicated to site personnel. To be managed in accordance with TP141, TP243 and CSSOW. | No exceptional risks recorded | x
17 | SGT3 installation, maintenance and repair | MEWP access to HV side of SGT3 completely blocked in current arrangement due to locations of abandoned UKPN owned gantry between SGT3 and SGT1. All work will have to be carried out from fixed platforms or scaffolding with associated risks on live compounds. |  | x |  | UKPN will be removing structures owned by them prior to the Works. | 2016-01-01 | National Grid |  | If the UKPN work does not take place National Grid together with the PC will have to identify new acces routes to the HV side of SGT3 | PEP and SGT3 layout PDD-6254-LAY-001 | x | x
18 | SGT3 132kV earth switch loccation | Impressed voltage management on SGT3 132kV cable connection; earth switch to be as close as possible to CSE |  | x | x | Earth switch relocated to reduce the risk. Maintain a drawing or schedule to identify the key impressed voltage risks and provide any details within the Hazard Register. Consider 132kV cable / GIS disconnection for isolation and earthing Disconnection of terminal tower to reduce voltages induced in parallel ccts? | 2015-09-01 | Jacobs | 2015-09-17
19 | 275/132kV compound lone working | Due to the high level of crime, location and lack of visibility National Grid currently don't undertake lone working at the 275/132kV compound. | x | x |  | National Grid and PC to consider hazard of lone working for guards at this compound during weekends and evenings. Guards may be doubled to mitigate. | 2015-10-02 | National Grid / PC | Construction | Personal safety of lone working staff at 275/132kV compound | PEP | x | x
20 | Excavation in both compounds | Service strikes due to unknown service routes. In particular, SGT3 bund pump cabling route unknown | x |  |  | Carry out GPR Survey | 2015-10-02 | National Grid /Jacobs |  | Survey fails to locae services or new services added between GPR survey and site start | Hazard drawings | x | x
21 | Above and below ground activities in the 275/132kV compound | The 275/132kV compound and surrounding auxiliary building areas contains open trenches, abandoned equipment, spillages, vegetation, lacks chippings, etc. that creates hazards to contractors working in the area. | x | x |  | Some of the areas are currently being cleared by UKPN. On cpmpletion the residual risks shall be identified. A joint PCI meeting is to be arranged with UKPN by National Grid. Any remaining obstructions and structures shall be removed and the area surface suitably prepared by the PC prior to the main construction start. | 2015-10-31 | National Grid / PC | Construction start | Some of the hazards may not be removed as part of the UKPN works. | None available | x
22 | Excavation of areas adjacent to SGT3 and SGT5 | Exposure to asbestos | x |  |  | Consult with ETAM Ops to determine the extent of asbestos within the land surrounding the SGT’s from their existing records e.g. asbestos management plan | 2015-10-31 | National Grid / PC | Construction | Asbestos exposure | Asbestos survey information included with the WI pack | x | x
23 | Access to SGT3 radiator for maintenance, inspection and repairs | The current design will create a platform that overhangs the bund creating confined space areas where injuries can be occur. |  | x |  | The transformer manufacturer will be requested to change the orientation of the platform but if this is not feasible an alternative solution may be required. The requirement has been recorded on the TP211 forms and drawings provided to National Grid. The latter has confirmed the arrangement with the manufacturer. | 2016-01-01 | Jacobs / National Grid | 2015-10-13 | Althouugh the manufacturer have confirmed these requirements the residual risks cannot be determined until the revised designs are available. | TP211 form | x | x
24 | Access to SGT5 MK and radiator | As the SGT5 MK will be located outside the FBW, detailed design of the cabling connection between the MK and the transformer will have to consider access and clearance. For example if a cable bridge is used 2.4m clearance will be required below it to allow safe passage. | x |  |  | MK cable connection to be designed allowing safe passage in the areas around the transformer and radiator requiring access. | 2015-10-31 | PC | Detailed Design | Design to be finalised so safe passage is not guaranteed. | SGT5a layout PDD-6253-LAY-001 | x
25 | Undertaking replacement of the transformer radiator fans (SGT3 and SGT5A) | Insufficient space to remove the fans due to the location of the radiator supports (SGT3 and SGT5a) and the modified stairs on SGT5a | x | x | x | Requirements added to TP211 form for Bulk Purchase contractor to consider these requirements. | 2015-10-31 | Jacobs/National Grid | 2015-10-13 | Insufficient space to remove the fans due to the location of the radiator supports (SGT3 and SGT5a) and the modified stairs on SGT5a | SGT5a TP211 forms | x
26 | Demolition of existing SGT’s (SGT3 and SGT5A) | Exposure to asbestos | x | x | x | Ensure an asbestos refurbishment survey is undertaken by a competent asbestos contractor prior to undertaken any intrusive works associated with the SGT’s | 2015-10-31 | National Grid / PC | Construction | Asbestos exposure | Asbestos survey information included with the WI pack | x | x
27 | Installation of oil draw off pipework at SGT5A | There is currently no information relating to underground service locations around the SGT5A transformer. Oil draw off pipework may need to be altered or the requirement removed if underground utilities make it difficult to provide a route that doesn't create additioinal hazards | x | x |  | Topographical and GPR information for the SGT5A areas appear to indicate there aren't significant risks associated with the installation of the oil draw off pipe.When Utility information is obtained from site surveys, PC shall check proposed route and discuss with NG Technical Assurance. | 2015-11-02 | Jacobs / National Grid / PC | Detailed Design Start | Oil draw off pipework may need to be altered or the requirement removed if underground utilities make it difficult to provide a suitable route | There is the possibility that services were not picked up during the GPR survey and therefore, normal HSG47 rules should still be adhered to for the entire oil draw off pipe route. Residual risk information is contained on Drg No. PDD/6253/LAY/005_Rev P1. | x
28 | Installation of oil draw off pipework at SGT3 | An underground utility service information drawing from National Grid (0901s013W_Phase2) shows a number of services, including the SGT4 CSE cables running through the proposed oil draw off route that create a hazard during construction. | x | x |  | Alternative routes were checked, but it would be extreamly difficult to get the oil draw off pipe from the existing bund to a suitable draw off location without crossing a number of services. Consulted NG Civil Assurance regarding the removal of the Oil Draw off pipe requirement due to the area around SGT3 being the very congested site services, particularly the CSE cables, but it was preferred to keep the oil draw off pipe. Other routes were considered but the original route was considered the most practical and safest to construct. | 2015-11-02 | Jacobs / National Grid | Detailed Design Start | Excavation hazard during construction. | Residual risk information is contained on Drg No. PDD/6254/LAY/005_Rev P1. | x | x
29 | Suitablilty of Transformer and cooler plinths for re-use (SGT3 & SGT5A). | The new transformer coolers are much bigger and heavier than the existing. No Geotechnical information is currently available for an accurate assessment to be made. | x |  |  | This hazard will be updated when the GI factual and interpretive reports become available. The GI is programmed to be undertaken w/c 11th Jan. 2016A structural assessment will be required to determine if the plinths are suitable for re-use | 2016-01-31 | Jacobs / National Grid |  | TBC | The GI is programmed to be undertaken w/c 11th Jan. Residual risks to be identified when factual and interpretive reports become available. | x | x
30 | Suitability of AIS foundation for re-use (SGT3 & SGT5A) | No geotechnical information is currently available for an accurate structural assessment to be made. | x |  |  | This hazard will be updated when the GI factual and interpretive reports become available. The GI is programmed to be undertaken w/c 11th Jan. A structural assessment will be required to determine if the AIS foundations are suitable for re-use | 2016-01-31 | Jacobs / National Grid |  | TBC | The GI is programmed to be undertaken w/c 11th Jan. Residual risks to be identified when factual and interpretive reports become available. | x | x
31 | Fire walls for SGT5A and SGT3 | No Geotechnical or underground services information is currently available for an assessment to be made on the suitability of proposed wall locations . | x |  |  | This hazard will be updated when the GI factual and interpretive reports become available. The GI is programmed to be undertaken w/c 11th Jan. Structural calculations and underground service checks will be required to determine if the locations and ground conditions are suitable | 2016-01-31 | Jacobs / National Grid |  | TBC | The GI is programmed to be undertaken w/c 11th Jan. Residual risks to be identified when factual and interpretive reports become available. | x | x