## Sheet1
SRM - 21 MOORFIELDS
RCL Tender Clarification Queries
Item | Description | SC Comments | BP Comments with RCL input | RCL comments 271220
1 | All timber products provided by RCL will be environmentally accredited. Usually this accreditation will be by FSC, if not it will be by one of the other recognised bodies, e.g. PEFC or CSA | Check with Tom King that this meets our sutainability requirements. | Our sustainability requirements have been provided by Tom and included onto the Vol 2. Our Sustainability requirements was also relayed to them in out PTM. | All timber products will be accredited in line with the sustainability requrements laid out in Volume 2
2 | Pricing Note 2. Where "access control" is noted on the pricing schedules RCL have allowed for mag locks, all other access control equipment is to be by others. Allgood have not quoted for mag locks we have therefore provided a provisional sum for the face fixed version, we have allowed for recessed ones to the metal doors. | Should any electronic strikes or push bars be included? | To be discussed in access control meeting with M&E and design team. | PH
4 | Pricing Note 3. Where required we have allowed to use our door manufacturer's certified intumescent and acoustic produced. We have allowed, only where necessary to achieve certification, intumescent sealant, we have not allowed for any other mastic. Mastic will not be fair faced. | Please confirm that seals will be provided in the door frame rather than the door? | RCL have confirmed this. | Closed out
5 | Pricing Note 4. Timber doors may be sourced from a separate company to that which supplies the frames however the whole doorset will be fully complaint in respect of fire certification, we not not allowed to achieve any specfic acoustic rating. As requred by the RFI's answered within the tendering period we have not allowed for PAS24 certification for timber doorsets. | Have the door frame, door specified ironmongery been fire tested as a complete set? Please refer to door schedule/spec for any acoustic criteria that needs to be met. | RCL will provide certification to demonstrate that they have been fire tested or certified approved fire tested. | Closed out? PH
6 | Project Specific Notes: All secondary steelwork or supporting structure to be supplied by others. Please note: It is the buyer's responsibility to ensure that the surrounding structure provides adequate support for the weight and frequency of use of the door and frame that sufficient grounds are in place for secure fixings. Structural openings should be square and plumb to ensure correct operation of the door. If door fitters have to leave site due to non-complaine with the above then stand down charges will result. All Assa Abloy non LPS1175 security door leafs will be manufactured to a thickness of 44mm and will perform a 'single swing' action c/w stainless steel butt hinges (dog bolt hinges for external doorsets). | RCL should be issued with set of drylining drawings to depic the goal post steel frames they will need to fix back to. | RCL have this information in their retention. | PH
7 | We have assumed that all Assa Abloy doorsets are to have a single rebated knockdown frame. Mitred and fully welded frame connections are available but will attract an extra over cost of £40 per frame. Please note LPS1175 SR4 doors have a single rebated welded frame. | SR4 doors will require to be fixed back to fully welded frames. | To be discussed in access control meeting with M&E and design team. | PH